|  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |
| --- | --- | --- | --- |
|  | Template of Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表模板 |  |  |
|  | Template No. | HYBN-T7-08-2003-2024-2 | Page 1 of 2 |

The following is the body of the template.

以下为模板正文。

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-1-001 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members 张浩然、于亚鹏、梁斌、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Name of unit (area)/process flow:circulating water field 单元（区域）/工艺过程名称：循环水场 |  |  |  | Unit/equipment/facility: P101A/B/C/D, P102A/B circulation pumps 装置/设备/设施：P101A/B/C/D、P102A/B循环水泵 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 001 | P101A/B/C/D, P102A/B Circulating water pump operation motor inspection P101A/B/C/D、P102A/B 循环水泵 |  | Motor bearing grease is not overflowing, refill record 电机轴承润滑脂是否溢出，加注记录 |  | Motor bearing burn 电机轴承烧 | Infrequent 偶尔 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Is the motor temperature and current in accordance with the requirements 电机温度，电流是否符合要求 |  | Overload, motor burn 超负荷，电机烧 | Rarely occur 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the motor vibration value as required 电机振动值是否符合要求 |  | Equipment damage 设备损坏 | Infrequent 偶尔 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | motor noise increasing 电机杂声是否增大 |  | Motor holding shaft 电机抱轴 | Infrequent 偶尔 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-1-002 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members 张浩然、于亚鹏、梁斌、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Name of unit (area)/process flow:circulating water field 单元（区域）/工艺过程名称：循环水场 |  |  |  | Unit/equipment/facility: P101A/B/C/D, P102A/B circulation pumps 装置/设备/设施：P101A/B/C/D、P102A/B循环水泵 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 002 | P101A/B/C/D, P102A/B Circulating water pump operation motor inspection P101A/B/C/D、P102A/B 循环水泵 |  | Whether the pump bearing grease is overflowing, refill record 机泵轴承润滑脂是否溢出，加注记录 |  | Worn and burned out bearings 轴承磨损、烧坏 | Rarely occur 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the pump bearing temperature as required机泵轴承温度是否符合要求 |  | Damaged bearings 轴承损坏 | Rarely occur 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Is the vibration value of the machine pump in accordance with the requirements机泵振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely occur 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the pump outlet pressure normal 机泵出口压力是否正常 |  | Equipment damage 设备损坏 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Leakage of machine seal 机封有无泄漏 |  | Machine seal damage 机封损坏 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-1-003 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members 张浩然、于亚鹏、梁斌、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Name of unit (area)/process flow:circulating water field 单元（区域）/工艺过程名称：循环水场 |  |  |  | Unit/equipment/facility: CWT101A~F 装置/设备/设施：CWT101A~F冷却塔 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 003 | CWT101A~F 冷却塔 CWT101A~F cooling towers |  | Are the wind turbines secure and free from damage 风筒是否损坏、有无破损 |  | Insufficient air volume and air pressure cause poor heat exchange and cooling effect of circulating water 风量、风压不足造成循环水换热降温效果差 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Check for even distribution of water 检查布水是否均匀 |  | Poor cooling effect of circulating water heat exchange 循环水换热降温效果差 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Inspect water receivers, nozzles, and fillers for breakage 检查收水器、喷头、填料有无破损情况 |  | Poor cooling effect of circulating water heat exchange 循环水换热降温效果差 | Infrequent 偶尔 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-1-004 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members 张浩然、于亚鹏、梁斌、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Name of unit (area)/process flow:circulating water field 单元（区域）/工艺过程名称：循环水场 |  |  |  | Unit/equipment/facility: AN101A~F 装置/设备/设施：AN101A~F冷却风机系统 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 004 | FAN101A~F Fan Inspection FAN101A~F 冷却风机系统 |  | Motor bearing grease is not overflowing, refill record 电机轴承润滑脂是否溢出，加注记录 |  | Motor bearing burn 电机轴承烧 | Infrequent 偶尔 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | 电机温度、电流是否正常 Is the motor |  | Overload, motor burn 超负荷，电机烧 | Infrequent 偶尔 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the motor vibration value as required temperature and current normal 电机振动值是否符合要求 |  | Equipment damage 设备损坏 | Infrequent 偶尔 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is motor noise increasing 电机杂声是否增大 |  | Motor holding shaft 电机抱轴 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Is the gearbox oil level normal 减速箱油位是否正常 |  | Reducer wear 减速机磨损 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Is the vibration of the speed reducer in accordance with the requirements 减速机振动是否符合要求 |  | Equipment damage 设备损坏 | Rarely occur 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-1-005 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members 张浩然、于亚鹏、梁斌、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Name of unit (area)/process flow:circulating water field 单元（区域）/工艺过程名称：循环水场 |  |  |  | Unit/equipment/facility:SR201A～H 装置/设备/设施：SR201A～H |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 005 | SR201A~H bypass filter SR201A~H 旁滤器 |  | Verify that the status of each pneumatic valve is normal 确认各气动阀门的状态是否正常 |  | Causes increased turbidity or "run-off" of circulating water 造成循环水浊度上升或“跑水” | Rarely occur 很少发生 | 2 | 1 | 2 | I |  |  |  |  |  |  |
|  |  |  | Is the differential pressure between the inlet and outlet of the bypass filter normal 旁滤器进出口压差是否正常 |  | Quartz sand slabbing and poor water discharge 石英砂板结，出水变差 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | 现场PLC控制面板显示、操作是否正常 Is the field PLC control panel display and operation normal |  | 现场无法手动操作或旁滤器运行程序混乱 Inability to operate manually on site or confusing by-pass filter operating procedures | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Verify that there are no "runs and leaks" 确认有无“跑冒滴漏” |  | Leakage 跑水 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-1-006 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members 张浩然、于亚鹏、梁斌、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Name of unit (area)/process flow:circulating water field 单元（区域）/工艺过程名称：循环水场 |  |  |  | Unit/equipment/facility: Dosing booth 装置/设备/设施：加药间 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 006 | Dosing room 加药间 |  | Doors and windows are not damaged and do not close 门窗有无损坏、关不上情况 |  | Broken doors and windows, rainwater in the dosing room 门窗坏、雨水淋到加药间 | Infrequent 偶尔 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Does the exhaust fan work properly 排风扇是否能正常工作 |  | Poor ventilation 通风不 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Eye wash water quality, water pressure is normal 洗眼器水质、水压否正常 |  | Eye wash not working properly 洗眼器无法正常使用 | Rarely occur 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the chemical stack meets the requirements 药剂堆放是否符合要求 |  | Wrong dosing of chemical 药剂投加错误 | Rarely occur 很少发生 | 2 | 3 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the liquid level of the medicament storage tank and the medicament pump are operating normally 药剂储罐液位、药剂泵运行是否正常 |  | The pump is damaged and the chemical cannot be added normally 泵损坏，药剂无法正常投加 | Infrequent 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Availability of safety signs 安全标识是否齐全 |  | Personal injury 人身伤害 | Rarely occu 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |