|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5101-001 |  | Unit:Utilities department 单位：公用工程部 | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis Date：Feb 10,2025 分析日期 : 2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:firefighting and water supply booster pumping station 单元（区域）/工艺过程名称：消防及给水加压泵站 |  |  | Inspection for operation of stabilized pressure fire pump P103A/B 消防稳压泵运行机泵检查 |  |  |  |  |  |  |  | Reviewed by:WangLiang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 001 | Inspection of the running motor of the fire stabilizing pump P103A/B P103A/B消防稳压泵运行电机检查 |  | Check whether the motor bearing grease overflows and fill in the record 电机轴承润滑脂是否溢出，加注记录 | Motor bearing burnt 电机轴承烧 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Check whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 | Overload, motor burning 超负荷，电机烧 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the motor vibration value meets the requirements 电机振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the noise of the motor has increased 电机杂声是否增大 | Motor shaft holder 电机抱轴 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Pump bearing grease filling record 机泵轴承润滑脂加注记录 | Bearing wear and burnout 轴承磨损、烧坏 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Check whether the pump temperature meet the requirements 机泵轴承温度是否符合要求 | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | II |  |  |  |  |  |  |
|  |  |  | Check whether the vibration value of the pump meets the requirements 机泵振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | II |  |  |  |  |  |  |
|  |  |  | Check whether the outlet pressure of the pump is normal 机泵出口压力是否正常 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | II |  |  |  |  |  |  |
|  |  |  | Check whether the machine seal is leaking 机封有无泄漏 | Damaged mechanical seal 机封损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5101-003 |  | Unit:Utilities department 单位：公用工程部 | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis Date：Feb 10,2025 分析日期 : 2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:firefighting and water supply booster pumping station 单元（区域）/工艺过程名称：消防及给水加压泵站 |  |  | Unit/equipment/facility:P101A, P102A~C Foam fire pump, fire water pump 装置/设备/设施：P101A、P102A~C泡沫消防泵、消防水泵 |  |  |  |  |  |  |  | Reviewed by:WangLiang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 002 | Motor inspection for foam fire pumps and fire pumps P101A P102A~C 泡沫消防泵、消防水泵运行电机检查 |  | Check whether the motor bearing grease overflows and fill the record 电机轴承润滑脂是否溢出，加注记录 | Motor bearing burnt 电机轴承烧 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Check whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 | Overload, motor burning 超负荷，电机烧 | Rarely occurs 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the motor vibration value meets the requirements电机振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the motor noise increases 电机杂声是否增大 | Motor shaft holder 电机抱轴 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Pump bearing grease filling record 机泵轴承润滑脂加注记录 | Bearing wear and burnout 轴承磨损、烧坏 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Check whether the temperature of the pump bearing meets the requirements 机泵轴承温度是否符合要求 | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the vibration value of the pump meets the requirements 机泵振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the outlet pressure of the pump is normal 机泵出口压力是否正常 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the machine seal is leaking 机封有无泄漏 | Damaged mechanical seal 机封损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5101-005 |  | Unit:Utilities department 单位：公用工程部 | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis Date：Feb 10,2025 分析日期 : 2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:firefighting and water supply booster pumping station 单元（区域）/工艺过程名称：消防及给水加压泵站 |  |  | Foam fire pump, diesel oil pump operation pump inspection P101B P102D~F 泡沫消防柴油泵、消防水柴油泵运行机泵检查 |  |  |  |  |  |  |  | Reviewed by:WangLiang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 003 | Foam fire pump, fire pump operation pump inspection P101A P102A~C 泡沫消防泵、消防水泵运行机泵检查 |  | The oil level of the diesel tank is at a proper position 柴油箱油位在合适位置 | Low diesel oil level stop pump 柴油油位低停泵 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Pump bearing grease filling record 机泵轴承润滑脂加注记录 | Bearing wear and burnout 轴承磨损、烧坏 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Check whether the temperature of the pump bearing meets the requirements 机泵轴承温度是否符合要求 | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the vibration value of the pump meets the requirements 机泵振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the outlet pressure of the pump is normal 机泵出口压力是否正常 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check Whether the machine seal is leaking 机封有无泄漏 | Damaged mechanical seal 机封损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5101-006 |  | Unit:Utilities department 单位：公用工程部 | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis Date：Feb 10,2025 分析日期 : 2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:firefighting and water supply booster pumping station 单元（区域）/工艺过程名称：消防及给水加压泵站 |  |  | Unit/equipment/facility:P301A~C, P302A~C Domestic water pump 装置/设备/设施： P301A~C、P302A~C生活水泵 |  |  |  |  |  |  |  | Reviewed by:WangLiang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 004 | Inspection of motor of domestic water pump P301A~C P302A~C 生活水泵运行电机检查 |  | Check whether the grease of the motor bearing overflows, fill the record 电机轴承润滑脂是否溢出，加注记录 | Motor bearing burnt 电机轴承烧 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Check whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 | Overload, motor burns 超负荷，电机烧 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the vibration value of the motor meets the requirements 电机振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the noise of the motor has increased 电机杂声是否增大 | Motor shaft 电机抱轴 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Pump bearing lubricant filling record 机泵轴承润滑油加注记录 | Bearing wear and burnout 轴承磨损、烧坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the temperature of the pump bearing meets the requirements 机泵轴承温度是否符合要求 | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the vibration value of the pump meets the requirements 机泵振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the outlet pressure of the pump is normal 机泵出口压力是否正常 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the mechanical seal is leaking 机封有无泄漏 | Damaged mechanical seal 机封损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5101-008 |  | Unit:Utilities department 单位：公用工程部 | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis Date：Feb 10,2025 分析日期 : 2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:firefighting and water supply booster pumping station 单元（区域）/工艺过程名称：消防及给水加压泵站 |  |  | Unit/equipment/facility:P401A~C, P402A/B, P403 Production pump 装置/设备/设施：P401A~C、P402A/B、P403生产水泵 |  |  |  |  |  |  |  | Reviewed by:WangLiang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 005 | Production water pump running motor inspection P401A~C P402A/B P403 生产水泵运行电机检查 |  | Check whether the grease of the motor bearing overflows, fill the record 电机轴承润滑脂是否溢出，加注记录 | Motor bearing burnt 电机轴承烧 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Check whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 | Overload, motor burns 超负荷，电机烧 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the vibration value of the motor meets the requirements 电机振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the noise of the motor has increased 电机杂声是否增大 | Motor shaft 电机抱轴 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Machine pump bearing lubricant filling record 机泵轴承润滑油加注记录 | Bearing wear and burnout 轴承磨损、烧坏 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Check whether the temperature of the pump bearing meets the requirements 机泵轴承温度是否符合要求 | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the vibration value of the pump meets the requirements 机泵振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the outlet pressure of the pump is normal 机泵出口压力是否正常 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the machine seal is leaking 机封有无泄漏 | Damaged mechanical seal 机封损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5101-010 |  | Unit:Utilities department 单位：公用工程部 | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis Date：Feb 10,2025 分析日期 : 2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:firefighting and water supply booster pumping station 单元（区域）/工艺过程名称：消防及给水加压泵站 |  |  | Unit/equipment/facility:T101A/B, T102A/B fire tank/production water tank, Domestic water tank 装置/设备/设施：T101A/B、T102A/B消防罐/生产水罐、生活水罐 |  |  |  |  |  |  |  | Reviewed by:WangLiang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 06 | Fire tank/production water tank, Domestic water tank T101A/B T102A/B 消防罐/生产水罐、生活水罐 |  | No cracks on the surface of the tank body 罐本体表面无裂纹 | The tank body is damaged 罐本体损坏 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Safety accessories such as level gauge are intact 液位计等安全附件完好 | Venting or take off 冒罐或抽空 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Electrostatic grounding is intact 静电接地完好 | Poor electrostatic grounding 静电接地不良 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | The valve is intact and the connecting flange has no leakage 阀门完好、连接法兰无泄漏 | Running hourglass 跑冒滴漏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |