|  |  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Hazard Analysis (JHA) Record Form 工作危害分析法 （JHA）记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Record No. |  | HYBN-T7-08-2002-2024-2 |  |  |  |  |  |  |  |  |  | Page 2 of 4 |  |  |  |  |
| No. 编号: | 12 |  | Department 部门: |  | Unit 装置: |  | Unit 装置: |  | Wastewater treatment plant污水处理场 ASU & ACU空分空压 |  |  |  |  |  | Analysis date： MM DD, YYYY 分析日期：2025年3月25日 |  |  |  |  |
| Task 工作任务: |  |  | Hot Work 动火作业 |  | Members of analysis group 分析小组成员: |  | Zhang Haoran, Liang Bin,Yu Yapeng,Li Guangyuan, Lv Yingqiang, Deng Wentao，Zhang Yunbo，Yin Zujun, Pan Wentao, Jiang Ruibin, Dou Jianqiang, Zhao Xueren, Chen Liao, Zhang Feipeng, Zhang Wenjun, Zhao Yu and team members 张浩然、梁斌、于亚鹏、李光远、吕应强、邓文涛、张云波、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁、陈聊、张飞鹏、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Reviewed by审核人： | Wang Liang 王亮 |  |  |  |
| S/N 序号 |  | Operation steps 工作步骤 |  | Hazard source or potential incident 危险源或潜在事件 |  | Major accident consequences 主要事故后果 |  | Former occurrence frequency 以往发生频率 |  | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 1 |  | Hot Work Planning and Risk Identification 动火作业计划与风险辨识 |  | Failure to formulate an operation plan in advance 未提前制定作业计划 |  | Misjudgment of risks and insufficient emergency preparedness 风险漏判、应急准备不足 |  | Rarely 很少发生 |  | 2 | 4 | 8 | Ⅱ | Fill out the fire plan in advance and clarify the risk control measures 提前填报动火计划，明确风险控制措施 |  | 1 | 2 | 2 | Ⅰ |
|  |  |  |  | Failure to comply with the approval procedures for emergency repairs resulted in inadequate preparation of emergency measures 紧急抢修未履行审批程序导致应急措施准备不充分 |  | Management out of control caused accidents 管理失控引发事故 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | 1. Implement the unplanned fire approval process执行非计划动火审批流程 2. Formulate an emergency response plan and conduct pre-operation briefing 制定应急处置预案并进行作业前交底 |  | 1 | 4 | 4 | Ⅰ |
| 2 |  | Preparation before hot work 动火作业前准备 |  | No hot work permit 未办理动火作业许可证 |  | Fire, explosion, casualties 火灾、爆炸、人员伤亡 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | According to the company's "Safety Management System", implement the fire operation approval system, and prohibit operations without permission 按照公司《安全管理制度》，执行动火作业审批制度，未经许可禁止作业 |  | 1 | 4 | 4 | Ⅰ |
|  |  |  |  | Work area not isolated or clearly marked 作业区域未隔离或标识不清 |  | Non-operating personnel entering the dangerous area 非作业人员进入危险区域 |  | Rarely 很少发生 |  | 2 | 4 | 8 | Ⅱ | 1. Set up a cordon to isolate and warn 设置警戒线隔离警戒 2. Arrange special personnel for supervision 安排专人监护 |  | 1 | 4 | 4 | Ⅰ |
| 3 |  | Hot work environment inspection 动火作业环境检查 |  | Combustibles not cleaned up 可燃物未清理 |  | Fire, explosion 火灾、爆炸 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | 1. No flammable gas should be discharged within 30m from the ignition point; no flammable liquid should be discharged within 15m from the ignition point; no flammable solvent cleaning or painting operations should be carried out at the same time within 10m from the ignition point and below the ignition point. 距动火点 30m 内 不应排放可燃气体；距动火点 15m 内 不应排放可燃液体；距动火点 10m 内 及动火点下方不应同时进行可燃溶剂清洗或喷漆等作业。 2. If there are flammable materials, cavities, manholes, trenches, water seals, etc. around or below the ignition point, they should be inspected and analyzed and measures such as cleaning or sealing should be taken; isolation measures should be taken for equipment and facilities that may leak flammable and combustible materials within 15m around the ignition point. 动火点周围或其下方地面如有可燃物、空洞、窨井、地沟、水封等，应进行检查分析并采取清理或封盖等措施；对于动火点周围 15m 范围内可能泄漏易燃、可燃物料的设备设施，应采取隔离措施。 3. Before starting a fire, implement measures one by one according to the principle of "who signs, who confirms" in the ignition operation ticket. 动火前按照动火作业票“谁签字谁确认”原则逐一落实措施 |  | 1 | 4 | 4 | Ⅰ |
|  |  |  |  | Poor ventilation leading to gas accumulation 通风不良环境导致气体聚集 |  | Poisoning, explosion 中毒、爆炸 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | 1. Sampling results must be obtained before entering the confined space. The qualified standards are CO < 30ppm, combustible gas < 10% LEL, H2S < 7PPM, benzene < 3mg/m3, oxygen 19.5%-21.5%. Unqualified systems are not allowed to enter without specifying special operation plans and implementing safety measures. 进入受限空间前必须有采样结果，合格标准为CO＜30ppm,可燃气＜10%LEL,H2S＜7PPM,苯＜3mg/m3，氧气19.5%-21.5%,不合格系统未指定特殊作业方案和落实安全措施不得进入 2. System testing should adopt multi-point testing and be representative 系统检测应该采用多点检测，具有代表性 |  | 1 | 4 | 4 | Ⅰ |
| 4 |  | Hot work facility inspection 动火设施检查 |  | Gas cylinders leaking or damaged 气瓶泄漏或破损 |  | Fire, explosion 火灾、爆炸 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | 1. Check the tightness of gas cylinders and pipelines before use, and check whether the on-site storage of acetylene cylinders and oxygen cylinders meets safety requirements 使用前检查气瓶及管线密封性，检查乙炔瓶和氧气瓶现场存放符合安全要求 2. Wear anti-static gloves. 佩戴防静电手套。 |  | 1 | 4 | 4 | Ⅰ |
|  |  |  |  | The insulation of the welding machine failed 电焊机绝缘失效 |  | Electric shock 触电 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | 1. Install leakage protection device and electrostatic grounding device安装漏电保护器和静电接地装置 2. Check the welding related equipment is intact before operation 作业前检查电焊相关设备完好 |  | 1 | 4 | 4 | Ⅰ |
| 5 |  | Hot work process 动火作业过程 |  | Sparks flew and ignited surrounding objects 火花飞溅引燃周边物品 |  | Fire 火灾 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | 1. Set up fire blanket, fire cloth, fire basin 设置防火毯、防火布、接火盆 2. The fire starter wears flame retardant clothing. 动火人穿戴阻燃服. 3. Equip fire extinguishing equipment and training 配备灭火器材并培训 |  | 1 | 4 | 4 | Ⅰ |
|  |  |  |  | The supervisor left his post without permission 监护人员擅离岗位 |  | Delayed emergency response 应急响应延迟 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | The guardian has passed the guardian training, clarified the guardianship responsibilities, and mastered the emergency measures 监护人经过监护培训合格，明确监护职责，并掌握应急措施 |  | 1 | 4 | 4 | Ⅰ |
| 6 |  | Cleaning up after hot work 动火作业后清理 |  | The remaining fire was not completely extinguished 余火未彻底熄灭 |  | Fire caused by re-ignition 复燃引发火灾 |  | Rarely 很少发生 |  | 2 | 5 | 10 | Ⅲ | After the fire is over, the on-duty staff will check and accept the construction site before closing the work ticket 动火结束后当班安排对施工现场检查验收后再关闭作业票 |  | 1 | 4 | 4 | Ⅰ |
|  |  |  |  | The waste was not disposed of in a standardized manner 废弃物未规范处置 |  | Environmental pollution or secondary fire 环境污染或二次火灾 |  | Rarely 很少发生 |  | 2 | 4 | 8 | Ⅱ | Classify and clean up the waste to the designated area 分类清理废弃物至指定区域 |  | 1 | 3 | 3 | Ⅰ |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the executable control measures that need to be added from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要增加的可执行控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety instructions: 安全告知： I have been informed of the hidden hazard source and harmful factors during the operation process, the corresponding safety measures and emergency evacuation methods. 我已经了解本项作业过程中的危险源、危害因素、相应的安全措施和应急疏散的途径。 Signature for confirmation: 签字确认： |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |