|  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |
| --- | --- | --- | --- |
|  | Template of Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表模板 |  |  |
|  | Template No. | HYBN-T7-08-2003-2024-2 | Page 1 of 2 |

The following is the body of the template.

以下为模板正文。

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5603-1 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team personnel 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date:Feb 10,2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:refrigeration station in device area 单元（区域）/工艺过程名称：装置区制冷站 |  |  |  | Unit/equipment/facility: P001A/B/, P002A/B chilled water pump 装置/设备/设施：P001A/B/、P002A/B冷冻水泵 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 001 | P001A/B P002A/B Chilled water P001A/B P002A/B 冷冻水泵运行电机检查 pump running motor inspection |  | Whether the grease of the motor bearing overflows, fill the record 电机轴承润滑油是否溢出，加注记录 |  | Motor bearing burnt 电机轴承烧 | Rarely happens很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 |  | Overload, motor burns 超负荷，电机烧 | Rarely happens很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the motor meets the requirements电机振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the noise of the motor has increased 电机杂声是否增大 |  | Motor shaft 电机抱轴 | Rarely happens很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5603-002 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team personnel 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date:Feb 10,2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:refrigeration station in device area 单元（区域）/工艺过程名称：装置区制冷站 |  |  |  | Unit/equipment/facility: P001A/B/, P002A/B chilled water pump 装置/设备/设施：P001A/B/、P002A/B冷冻水泵 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 002 | P001A/B P002A/B Chilled water pump running machine pump inspection P001A/B P002A/B 冷冻水泵运行机泵检查 |  | Whether the lubricating grease of the machine pump bearing overflows, fill the record机泵轴承润滑油是否溢出，加注记录 |  | Bearing wear and burnout轴承磨损、烧坏 | Rarely happens很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the temperature of the pump bearing meets the requirements机泵轴承温度是否符合要求 |  | Bearing damage轴承损坏 | Rarely happens很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the pump meets the requirements机泵振动值是否符合要求 |  | Equipment damage设备损坏 | Rarely happens很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the outlet pressure of the pump is normal机泵出口压力是否正常 |  | Equipment damage设备损坏 | Rarely happens很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | 机封有无泄漏 Whether the machine seal is leaking |  | 机封损坏 Damaged mechanical seal | Occasionally偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5603-003 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team personnel 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date:Feb 10,2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:refrigeration station in device area 单元（区域）/工艺过程名称：装置区制冷站 |  |  |  | Installation/Equipment/Facilities:WCH-001A/B, 002A/B 装置/设备/设施：WCH-001A/B、002A/B |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 003 | WCH-001A/BWCH-002A/B Hot water type lithium bromide absorption chiller WCH-001A/BWCH-002A/B 热水型溴化锂吸收式制冷机 |  | I s the hot water temperature of the refrigerator normal制冷机热水温度是否正常 |  | Affect the concentration of refrigerant影响冷剂的浓度 | Rarely happens很少发生 | 2 | 3 | 4 | I |  |  |  |  |  |  |
|  |  |  | 制冷机冷水温度是否正常 Whether the cold water temperature of the refrigerator is normal |  | 影响冷冻水的温度 Affect the temperature of chilled water | Rarely happens很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the vacuum of the refrigerator suitable制冷机真空度是否合适 |  | Affect the efficiency of the refrigerator影响制冷机的效率 | Rarely happens很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5603-004 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: SCL分析小组人员：ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team personnel 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date:Feb 10,2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:refrigeration station in device area 单元（区域）/工艺过程名称：装置区制冷站 |  |  |  | 装置/设备/设施：PA-001 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 004 | PA-001 Constant pressure water supplement device inspection PA-001 定压补水装置检查 |  | Whether the liquid level of the water tank is normal水箱液位是否正常 |  | Low pressure in chilled water network冷冻水管网压力低 | Rarely happens很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the outlet pressure of the constant pressure make-up pump normal定压补水泵出口压力是否正常 |  | Low or high pipe network pressure管网压力低或高 | Rarely happens很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the motor meets the requirements电机振动值是否符合要求 |  | Equipment damage设备损坏 | Rarely happens很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the noise of the motor has increased电机杂声是否增大 |  | Motor shaft电机抱轴 | Occasionally偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |