|  |  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Hazard Analysis (JHA) Record Form 工作危害分析法 （JHA）记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Record No. |  | HYBN-T7-08-2002-2024-2 |  |  |  |  |  |  |  |  |  | Page 2 of 4 |  |  |  |  |
| No. 编号: | 20 |  | Department 部门: |  | Utilities Department 公用工程部 |  | Unit 装置: |  | Wastewater treatment plant污水处理场 ASU & ACU空分空压 |  |  |  |  |  | Analysis date： MM DD, YYYY 分析日期：2025年3月25日 |  |  |  |  |
| Task 工作任务: |  |  | Temporary power supply work 临时用电作业 |  | Members of analysis group 分析小组成员: |  | Zhang Haoran, Liang Bin,Yu Yapeng,Li Guangyuan, Lv Yingqiang, Deng Wentao，Zhang Yunbo，Yin Zujun, Pan Wentao, Jiang Ruibin, Dou Jianqiang, Zhao Xueren, Chen Liao, Zhang Feipeng, Zhang Wenjun, Zhao Yu and team members 张浩然、梁斌、于亚鹏、李光远、吕应强、邓文涛、张云波、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁、陈聊、张飞鹏、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Reviewed by 审核人： | Wang Liang 王亮 |  |  |  |
| S/N 序号 |  | Operation steps 工作步骤 |  | Hazard source or potential incident 危险源或潜在事件 |  | Major accident consequences 主要事故后果 |  | Former occurrence frequency 以往发生频率 |  | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 1 |  | Preparation before operation 作业前准备 |  | Failure to inspect electrical equipment and lines, equipment or lines with insulation damage, aging and other problems may cause leakage 未对用电设备及线路进行检查，设备或线路存在绝缘破损、老化等问题，可能导致漏电 |  | Electric shock 触电 |  | Occasionally 偶尔发生 |  | 3 | 4 | 12 | Ⅲ | 1. Re-identify risks before operation. 作业前重新识别风险。 2. Perform a comprehensive inspection of all electrical equipment and lines before operation to check for damage, aging, loose joints, etc. 作业前对所有用电设备和线路进行全面检查，查看是否有破损、老化、接头松动等情况。 3. Use tools such as insulation resistance testers to test the insulation performance of equipment and lines to ensure good insulation. 使用绝缘电阻测试仪等工具对设备和线路的绝缘性能进行测试，确保绝缘良好。 |  | 2 | 2 | 4 | Ⅰ |
| 2 |  | Temporary work ticket approval 临时作业票审批 |  | Temporary power operation without temporary power operation permit 未办理临时用电作业许可证 |  | Electric shock, fire and explosion 触电、火灾爆炸 |  | Rarely occurs很少发生 |  | 2 | 5 | 10 | Ⅲ | Execute the relevant regulations on temporary power use issued by the Ministry of Electricity 执行电气部发布的有关临时用电相关规定 |  | 2 | 2 | 4 | Ⅰ |
|  |  |  |  | Failure to identify the on-site environment (such as flammable gas, accumulated water) 未辨识现场环境（如易燃气体、积水） |  | Electrical fire, electric shock 电气火灾、触电 |  | Rarely occurs很少发生 |  | 2 | 5 | 10 | Ⅲ | For temporary power use in explosion-proof areas, obtain the corresponding approved hot work permit before supplying power 防爆区域临时用电属地办理相应的审批合格的动火作业票后再送电 |  | 2 | 2 | 4 | Ⅰ |
| 3 |  | Distribution box and switch settings 配电箱及开关设置 |  | The distribution box is not equipped with a leakage protector or the leakage protector fails, and the switch is improperly selected, which may result in the failure to cut off the power supply in time when leakage occurs 配电箱未安装漏电保护器或漏电保护器失灵，开关选型不当，可能导致漏电时无法及时切断电源 |  | Electric shock 触电 |  | Rarely occurs很少发生 |  | 2 | 4 | 8 | Ⅱ | 1. Select a qualified distribution box and install a leakage protector with a leakage action current of no more than 30mA and an action time of no more than 0.1s in accordance with regulations. 选用合格的配电箱，并按照规定安装漏电动作电流不大于30mA、动作时间不大于0.1s的漏电保护器。 2. Test the leakage protector regularly. 定期对漏电保护器进行测试。 3. Select a switch with a suitable rated current and type according to the power and working characteristics of the electrical equipment. 根据用电设备的功率和工作特性，选择合适额定电流和类型的开关。 |  | 2 | 2 | 4 | Ⅰ |
| 4 |  | Line laying 线路敷设 |  | The temporary power line does not meet the requirements 临时用电线路敷设不符合要求 |  | Leakage or short circuit 漏电或短路 |  | Rarely occurs很少发生 |  | 2 | 4 | 8 | Ⅱ | 1. Temporary power lines should be laid overhead or underground. The overhead height should meet safety requirements, and buried lines should be protected by pipes. 临时用电线路应采用架空或埋地敷设，架空高度满足安全要求，埋地时应穿管保护。 2. When crossing roads, measures such as adding protective casings should be taken to prevent the lines from being crushed by vehicles. 穿越道路时，应采取加设防护套管等措施，防止线路被车辆碾压。 |  | 2 | 2 | 4 | Ⅰ |
| 5 |  | Equipment installation and connection 设备安装与连接 |  | The electrical equipment is not installed firmly and the wiring is not standardized 用电设备安装不稳固，接线不规范 |  | Equipment tipping over and injuring people or poor contact causing fire 设备倾倒伤人或接触不良引发火灾 |  | Rarely occurs很少发生 |  | 2 | 4 | 8 | Ⅱ | 1. Install the electrical equipment on a stable and firm foundation, and take fixing measures if necessary. 将用电设备安装在平稳、牢固的基础上，必要时采取固定措施。 2. Carry out wiring in accordance with the electrical installation specifications, ensure that the wire ends are firmly connected and not exposed, and wrap them with insulating tape. 按照电气安装规范进行接线，确保线头连接牢固，无裸露，使用绝缘胶带进行包扎。 3. After the installation is completed, conduct a trial run inspection of the equipment to ensure normal operation. 安装完成后，对设备进行试运行检查，确保运行正常。 |  | 2 | 2 | 4 | Ⅰ |
| 5 |  | Power-on operation 通电操作 |  | The operators have not received professional training, do not have electrical knowledge, and operate in violation of regulations 作业人员未经过专业培训，不具备电气知识，违规操作 |  | Electric shock 触电 |  | Rarely occurs很少发生 |  | 2 | 4 | 8 | Ⅱ | 1. Provide special safety training for temporary power workers, and they can only take up their posts after passing the assessment. 对临时用电作业人员进行专门的安全培训，考核合格后方可上岗。 2. Arrange special personnel to supervise the operation process and correct violations in a timely manner. 安排专人对作业过程进行监督，及时纠正违规行为。 |  | 2 | 2 | 4 | Ⅰ |
| 6 |  | Operation process monitoring 作业过程监护 |  | There is no dedicated person to supervise during the operation, and safety hazards such as equipment failure and illegal operation of personnel cannot be discovered in time 作业过程中无专人监护，无法及时发现设备故障、人员违规操作等安全隐患 |  | Leading to the expansion of accidents 导致事故扩大 |  | Rarely occurs很少发生 |  | 2 | 4 | 8 | Ⅱ | 1. Appoint a specific person to monitor the entire process of temporary power operation. 明确专人负责临时用电作业的全过程监护。 2. The supervisor should have electrical safety knowledge and emergency handling capabilities and should not leave the post without authorization. 监护人员应具备电气安全知识和应急处理能力，不得擅自离岗。 3. If the supervisor finds an abnormal situation, he should immediately stop the operation and take measures to deal with it. 监护人员发现异常情况应立即停止作业，采取措施进行处理。 |  | 2 | 2 | 4 | Ⅰ |
| 7 |  | Job end 作业结束 |  | Failure to cut off power supply in time after the operation is completed and dismantle temporary power lines 作业结束后未及时切断电源，拆除临时用电线路 |  | Causing unrelated personnel to accidentally touch and get electric shock, or long-term exposure of the line causing safety accidents 导致无关人员误触触电，或线路长期暴露引发安全事故 |  | Rarely occurs很少发生 |  | 2 | 4 | 8 | Ⅱ | 1. After the operation is completed, cut off the power supply immediately and remove the temporary power lines and equipment. 作业结束后，立即切断电源，拆除临时用电线路和设备。 2. Properly store the removed lines and equipment for next use. 对拆除的线路和设备进行妥善保管，以备下次使用。 3. Clean up the operation site and restore it to its original state. 对作业现场进行清理，恢复原状。 |  | 2 | 2 | 4 | Ⅰ |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the executable control measures that need to be added from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要增加的可执行控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety instructions: 安全告知： I have been informed of the hidden hazard source and harmful factors during the operation process, the corresponding safety measures and emergency evacuation methods. 我已经了解本项作业过程中的危险源、危害因素、相应的安全措施和应急疏散的途径。 Signature for confirmation: 签字确认： |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |