|  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |
| --- | --- | --- | --- |
|  | Template of Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表模板 |  |  |
|  | Template No. | HYBN-T7-08-2003-2024-2 | Page 1 of 2 |

The following is the body of the template.

以下为模板正文。

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5601-001 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Unit (area)/process name: hot water station 单元（区域）/工艺过程名称：热水站 |  |  |  | Installation/equipment/facilities: P101A/B/C/D hot water pump 装置/设备/设施：P101A/B/C/D热水泵 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 001 | Hot water pump running motor inspection P-101A/B/C/D 热水泵运行电机检查 |  | Whether the motor bearing grease overflows, fill the record 电机轴承润滑油是否溢出，加注记录 |  | Motor bearing burns 电机轴承烧 | Rarely occur 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 |  | Overload, motor burns 超负荷，电机烧 | Rarely occur 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the motor vibration value meets the requirements 电机振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely occur 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the noise of the motor has increased 电机杂声是否增大 |  | Motor shaft locked 电机抱轴 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  | II |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5601-002 |  | Unit: Utilities Department 单位:公用工程部 |  | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Unit (area)/process name: hot water station 单元（区域）/工艺过程名称：热水站 |  |  |  | Installation/equipment/facilities: P101A/B/C/D hot water pump 装置/设备/设施：P101A/B/C/D热水泵 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 002 | Hot water pump running machine pump inspection P-101A/B/C/D 热水泵运行机泵检查 |  | Machine pump bearing lubricating oil filling record 机泵轴承润滑油加注记录 |  | Bearing wear and burnout 轴承磨损、烧坏 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the pump bearing temperature meets the requirements 机泵轴承温度是否符合要求 |  | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the pump outlet pressure is normal 机泵出口压力是否正常 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the machine seal is leaking 机封有无泄漏 |  | Mechanical seal damage 机封损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Machine pump bearing lubricating oil filling record 机泵轴承润滑油加注记录 |  | Bearing wear and burnout 轴承磨损、烧坏 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5601-003 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Unit (area)/process name: hot water station 单元（区域）/工艺过程名称：热水站 |  |  |  | Device/equipment/facilities: PA-101A/B condensate recovery lift pump 装置/设备/设施：PA-101A/B凝结水回收提升泵 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 003 | PA-101A/B 凝结水回收提升泵 Condensate recovery lift pump |  | Whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 |  | Overload, motor burns超负荷，电机烧 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the motor vibration value meets the requirements 电机振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the pump bearing grease overflows, fill the record 机泵轴承润滑脂是否溢出，加注记录 |  | Bearing wear and burnout 轴承磨损、烧坏 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the pump bearing temperature meets the requirements 机泵轴承温度是否符合要求 |  | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the pump meets the requirements机泵振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the outlet pressure of the pump is normal 机泵出口压力是否正常 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5601-004 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Unit (area)/process name: hot water station 单元（区域）/工艺过程名称：热水站 |  |  |  | Installation/equipment/facilities: E-101 steam heater 装置/设备/设施：E-101蒸汽加热器 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 004 | E-101 Steam heater蒸汽加热器 |  | Leakage of tube side and shell side管程、壳程泄漏情况 |  | Hot water string to the steam condensate pipe network 热水串到蒸汽凝液管网 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Heat transfer efficiency 换热效率 |  | Poor heat exchange effect 换热效果差 | Rarely happens 很少发生 | 2 | 2 | 4 | I |  |  |  |  |  |  |
|  |  |  | Whether the heater shakes 加热器有无晃动 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | The valve is intact and the connecting flange has no leakage 阀门完好、连接法兰无泄漏 |  | Runoff drip/leaking 跑冒滴漏 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5601-005 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年2月 10日 |  |  |  |  |
| Unit (area)/process name: hot water station 单元（区域）/工艺过程名称：热水站 |  |  |  | Installation/equipment/facilities: D-101 hot water buffer tank 装置/设备/设施：D-101热水缓冲罐 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 005 | D-101 热水缓冲罐 Hot water buffer tank |  | Whether the pressure is within the specified range 压力是否在规定范围 |  | Overpressure, safety valve jumps; negative pressure, tank damage超压，安全阀起跳；负压，罐损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the liquid level is within the specified range 液位是否在规定范围 |  | High liquid level causes the overflow valve interlock to trigger; low liquid level causes the hot water pump to evacuate 高液位导致溢流阀联锁触发；低液位导致热水泵抽空 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Confirmation of safety accessories operating status 安全附件运行状态确认 |  | The pressure gauge shall not cause overpressure and negative pressure; the liquid level gauge shall not cause the high level interlock to trigger or the low level pump evacuates; the safety valve does not jump when the trigger pressure is reached, and the tank is damaged 压力表不准造成超压、负压；液位计不准造成高液位联锁触发或低液位泵抽空；达到起跳压力安全阀未起跳造，成罐损坏 | Occasionally 偶尔 | 3 | 3 | 9 | III | 1.Every Monday, day shift conduct petrol inspections at height, check pressure and liquid level with on-site and central control每周一白班高处巡检检查，现场与中控核对压力、液位 2.The safety valve shall be calibrated regularly, and the high-altitude patrol inspection of the team shall be checked regularly安全阀定期校验，定期抽查班组高处巡检情况。 |  | 2 | 2 | 4 | I |
|  |  |  | The valve is intact and the connecting flange has no leakage 阀门完好、连接法兰无泄漏 |  | Runoff drip/leaking 跑冒滴漏 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5601-006 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Feb 10,2025 分析日期： 2025 年 2月 10日 |  |  |  |  |
| Unit (area)/process name: hot water station 单元（区域）/工艺过程名称：热水站 |  |  |  | Installation/Equipment/Facilities: PA-101 condensed water return to collection tank 装置/设备/设施：PA-101凝结水回收集水罐 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 006 | PA-101 Condensate return to the collection tank凝结水回收集水罐 |  | 液位是否在规定范围 Whether the liquid level is within the specified range |  | 高液位导致冒罐；低液位导致水泵抽空 High liquid level leads to tank overflow; Low liquid level causes the pump to empty | Infrequent 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Confirmation of safety accessories operating status 安全附件运行状态确认 |  | The liquid level gauge shall not cause the high liquid level tank to overflow or the low liquid level pump to evacuate; When the take-off pressure is reached, the safety valve does not take off and the tank is damaged 液位计不准造成高液位冒罐或低液位泵抽空；达到起跳压力安全阀未起跳造，成罐损坏 | Rarely occur 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | The valve is intact and the connecting flange has no leakage 阀门完好、连接法兰无泄漏 |  | Runoff drip/leaking 跑冒滴漏 | Infrequent 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5601-007 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group: ZhangHaoran,Liangbin,Yuyapeng,LiguangyuanLvyingqiang,Yinzujun,PanWentao,Jiangruibin,Dou Jianqiang, Zhaoxueren and team members SCL分析小组人员： 张浩然、梁斌、于亚鹏、李光远、吕应强、尹祖君、潘文涛、蒋瑞兵、窦建强、赵学仁及班组人员 |  |  |  |  |  |  |  | Analysis date: Jan 10,2025 分析日期： 2025 年2月10日 |  |  |  |  |
| Unit (area)/process name: hot water station 单元（区域）/工艺过程名称：热水站 |  |  |  | Installation/Equipment/Facilities: Stairs, Platforms 装置/设备/设施：楼梯、平台 |  |  |  |  |  |  |  | Reviewed by:Wang Liang 审核人：王亮 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 007 | Stairs, platforms 楼梯、平台 |  | Whether the guardrail shakes or rusts 护栏有无晃动、锈蚀 |  | Personnel falling 人员跌落 | Rarely happens很少发生 | 2 | 2 | 4 | I |  |  | 1 | 3 | 3 | I |
|  |  |  | Whether the pedal platform is damaged or corroded 踏板平台有无破损、锈蚀 |  | Personnel falling 人员坠落 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the lighting lamp shakes and illuminates normally 照明灯有无晃动、是否正常照明 |  | Personnel tripping and falling 人员绊倒、跌落 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether there are any objects stacked on the platform 平台上有无物体堆放 |  | Object strike 物体打击 | Rarely happens很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |