|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-2-001 |  | Unit:：Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Second Circulating Water 单元（区域）/工艺过程名称：二循环水场 |  |  |  | Unit/equipment/facility:P201A/B/C, P202 circulating water pump motor 装置/设备/设施：P201A/B/C、P202循环水泵电机 |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 1 | P201A/B/C、P202 Circulating water pump running motor inspection P201A/B/C、P202 循环水泵运行电机检查 |  | Whether the motor bearing grease is overflowing, fill in the record 电机轴承润滑脂是否溢出，加注记录 | Motor bearing burnt 电机轴承烧 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 | Overload, motor burns 超负荷，电机烧 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the motor meets the requirements 电机振动值是否符合要求 | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the noise of the motor has increased 电机杂声是否增大 | Motor shaft 电机抱轴 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-2-002 |  | Unit:：Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Second Circulating Water 单元（区域）/工艺过程名称：二循环水场 |  |  |  | Unit/equipment/facility: P201A/B/C, P202 circulating water pump 装置/设备/设施：P201A/B/C、P202循环水泵 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 2 | P201A/B/C、P202 Circulating water pump running machine pump inspection P201A/B/C、P202 循环水泵运行机泵检查 |  | Whether the lubricating grease of the machine pump bearing overflows, fill the record 机泵轴承润滑脂是否溢出，加注记录 |  | Bearing wear and burnout 轴承磨损、烧坏 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Whether the temperature of the pump bearing meets the requirements 机泵轴承温度是否符合要求 |  | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the pump meets the requirements 机泵振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the outlet pressure of the pump is normal 机泵出口压力是否正常 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the machine seal is leaking 机封有无泄漏 |  | Damaged mechanical seal 机封损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-2-003 |  | Unit:：Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Second Circulating Water 单元（区域）/工艺过程名称：二循环水场 |  |  |  | Unit/equipment/facility:CWT201A/B cooling tower 装置/设备/设施：CWT201A/B冷却塔 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 3 | CWT201A/B Cooling tower inspection CWT201A/B 冷却塔检查 |  | Whether the air duct is firm and whether it is damaged 风筒是否牢固、有无破损情况 |  | Insufficient air volume and air pressure cause poor heat exchange and cooling effects of circulating water 风量、风压不足造成循环水换热降温效果差 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the water distribution is even 检查布水是否均匀 |  | Circulating water has poor heat exchange and cooling effect 循环水换热降温效果差 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Check whether the skimmer, nozzle and packing are damaged 检查收水器、喷头、填料有无破损情况 |  | Circulating water has poor heat exchange and cooling effect 循环水换热降温效果差 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-2-004 |  | Unit:：Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Second Circulating Water 单元（区域）/工艺过程名称：二循环水场 |  |  |  | Unit/equipment/facility:FAN201A/B Fan 装置/设备/设施：FAN201A/B风机 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 4 | FAN201A/B Fan inspection FAN201A/B 风机检查 |  | Whether the grease of the motor bearing overflows, fill the record 电机轴承润滑脂是否溢出，加注记录 |  | Motor bearing burnt 电机轴承烧 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Whether the motor temperature and current are normal 电机温度、电流是否正常 |  | Overload, motor burns 超负荷，电机烧 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the motor meets the requirements电机振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the noise of the motor has increased 电机杂声是否增大 |  | Motor shaft 电机抱轴 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the oil level of the gearbox is normal 减速箱油位是否正常 |  | Reducer wear 减速机磨损 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the vibration of the reducer meets the requirements 减速机振动是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-2-005 |  | Unit:：Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Second Circulating Water 单元（区域）/工艺过程名称：二循环水场 |  |  |  | Unit/equipment/facility:SR201A/B/C Bypass filter 装置/设备/设施：SR201A/B/C旁滤器 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 5 | SR201A/B/C Bypass filter SR201A/B/C 旁滤器 |  | Confirm whether the status of each pneumatic valve is normal 确认各气动阀门的状态是否正常 |  | Cause the turbidity of circulating water to rise or "running water" 造成循环水浊度上升或“跑水” | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the pressure difference between the inlet and outlet of the side filter normal 旁滤器进出口压差是否正常 |  | Quartz sand is hardened and the effluent becomes worse 石英砂板结，出水变差 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the on-site PLC control panel displays and operates normally 现场PLC控制面板显示、操作是否正常 |  | Unable to manually operate on site or the side filter operation program is chaotic 现场无法手动操作或旁滤器运行程序混乱 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Confirm whether there is "running dripping" 确认有无“跑冒滴漏” |  | Running water 跑水 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5111-2-006 |  | Unit:：Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Second Circulating Water 单元（区域）/工艺过程名称：二循环水场 |  |  |  | Unit/equipment/facility:Dosing room 装置/设备/设施：加药间 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 6 | Dosing Room 加药间 |  | Whether the doors and windows are damaged or cannot be closed 门窗有无损坏、关不上情况 |  | Broken doors and windows, rainwater dripping into the dosing room 门窗坏、雨水淋到加药间 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the exhaust fan can work normally 排风扇是否能正常工作 |  | Poor ventilation 通风不畅 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the eyewash water quality and water pressure normal 洗眼器水质、水压否正常 |  | The eyewash cannot be used normally 洗眼器无法正常使用 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the dosing stack meets the requirements 药剂堆放是否符合要求 |  | Wrong dosage 药剂投加错误 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the liquid level of the dosing storage tank and the medicament pump are operating normally 药剂储罐液位、药剂泵运行是否正常 |  | The pump is damaged and the dosing cannot be added normally 泵损坏，药剂无法正常投加 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the safety mark complete 安全标识是否齐全 |  | Personal injury 人身伤害 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |