|  |  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Hazard Analysis (JHA) Record Form 工作危害分析法 （JHA）记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Record No. |  | HYBN-T7-08-2002-2024-2 |  |  |  |  |  |  |  |  |  | Page 2 of 4 |  |  |  |  |
| No. 编号: | 5111-2-001 |  | Department 部门: |  | Utilities Department 公用工程部 |  | Unit 装置: |  | Second Circulating Water 二循环水场 |  |  |  |  |  | Analysis date： 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Task 工作任务: |  |  | Sodium hypochlorite discharge 次氯酸钠卸料 |  | Members of analysis group 分析小组成员: |  | Zhang Haoran, Yu Yapeng, Deng Wentao, Zhang Yunbo, Chen Liao, Liangbing、Zhang Feipeng, Zhang Wenjun, Zhao Yu and team members 张浩然、于亚鹏、邓文涛、张云波、梁斌、陈聊、张飞鹏、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Reviewed by 审核人： | Wen Jiancheng, 温建成 |  |  |  |
| S/N 序号 |  | Operation steps 工作步骤 |  | Hazard source or potential incident 危险源或潜在事件 |  | Major accident consequences 主要事故后果 |  | Former occurrence frequency 以往发生频率 |  | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 1 |  | Wear PPE 穿戴PPE |  | PPE not worn PPE未穿戴 |  | Skin corrosion 皮肤腐蚀 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 2 |  | Arrange guardianship 安排监护 |  | No guardianship 未安排监护 |  | Takeoff 冒罐 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 3 |  | Check that the unloading pump, pipeline and valve should be intact and there is no leakage 检查卸料泵、管路、阀门应完好，无泄漏 |  | Leakage in discharge line 卸料管线泄漏 |  | Polluted environment 污染环境 |  | Rarely happens 很少发生 |  | 2 | 4 | 8 | II |  |  |  |  |  |  |
| 4 |  | Slowly inject into the tank and do the metering 缓慢注入储罐中同时做好计量 |  | Quick injection into the storage tank 注入储罐速度较快 |  | Takeoff 冒罐 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the executable control measures that need to be added from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要增加的可执行控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety instructions: 安全告知： I have been informed of the hidden hazard source and harmful factors during the operation process, the corresponding safety measures and emergency evacuation methods. 我已经了解本项作业过程中的危险源、危害因素、相应的安全措施和应急疏散的途径。 Signature for confirmation: 签字确认： |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Hazard Analysis (JHA) Record Form 工作危害分析法 （JHA）记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Record No. |  | HYBN-T7-08-2002-2024-2 |  |  |  |  |  |  |  | Page 2 of 4 |  |  |  |  |
| No. 编号: | 5111-2-002 |  | Department 部门: |  | Utilities Department 公用工程部 | Unit 装置: |  | Second Circulating Water 二循环水场 |  |  |  |  | Analysis date： 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Task 工作任务: |  |  | Rotate 盘车 |  | Members of analysis group 分析小组成员: | Zhang Haoran, Yu Yapeng, Deng Wentao, Zhang Yunbo, Chen Liao, Liangbing、Zhang Feipeng, Zhang Wenjun, Zhao Yu and team members 张浩然、于亚鹏、邓文涛、张云波、梁斌、陈聊、张飞鹏、张文俊、赵宇及班组成员 |  |  |  |  |  |  | Reviewed by 审核人： | Wen Jiancheng, 温建成 |  |  |  |
| S/N 序号 |  | Operation steps 工作步骤 |  | Hazard source or potential incident 危险源或潜在事件 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 |  | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  |  |  | L | S | R | Level等级 |  | L | S | R | Level等级 |
| 1 |  | Contact between panel and field operators 内外操联系 |  | Internal and external operations are not contacted, the internal operations manually start the equipment 内外操未联系，内操手动启动设备 |  | Mechanical damage 机械伤害 | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |
| 2 |  | Switch to manual 切手动 |  | At site did not put "Manual" or "Stop" 现场未打到“手动”或“停止” |  | Mechanical damage 机械伤害 | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |
| 3 |  | Determine the operating status 确定运行状态 |  | The equipment is running 设备处于运行状态 |  | Mechanical damage 机械伤害 | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |
| 4 |  | Turn 2-3 times 盘车2-3圈 |  | Failure to rotate 2-3 times as required 未按规定盘车2-3圈 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the executable control measures that need to be added from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要增加的可执行控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety instructions: 安全告知： I have been informed of the hidden hazard source and harmful factors during the operation process, the corresponding safety measures and emergency evacuation methods. 我已经了解本项作业过程中的危险源、危害因素、相应的安全措施和应急疏散的途径。 Signature for confirmation: 签字确认： |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Hazard Analysis (JHA) Record Form 工作危害分析法 （JHA）记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Record No. |  | HYBN-T7-08-2002-2024-2 |  |  |  |  |  |  |  |  |  | Page 2 of 4 |  |  |  |  |
| No. 编号: | 5111-2-003 |  | Department 部门: |  | Utilities Department 公用工程部 |  | Unit 装置: |  | Second Circulating Water 二循环水场 |  |  |  |  |  | Analysis date： 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Task 工作任务: |  |  | Switch pump 切泵 |  | Members of analysis group 分析小组成员: |  | Zhang Haoran, Yu Yapeng, Deng Wentao, Zhang Yunbo, Chen Liao, Liangbing、Zhang Feipeng, Zhang Wenjun, Zhao Yu and team members 张浩然、于亚鹏、邓文涛、张云波、梁斌、陈聊、张飞鹏、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Reviewed by 审核人： |  | Wen Jiancheng, 温建成 |  |  |
| S/N 序号 |  | Operation steps 工作步骤 |  | Hazard source or potential incident 危险源或潜在事件 |  | Major accident consequences 主要事故后果 |  | Former occurrence frequency 以往发生频率 |  | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 1 |  | Check and confirm 检查确认 |  | Failure to check the status of the backup pump 未检查确认备用泵状态 |  | Damaged pump 机泵损坏 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 2 |  | Start the standby pump 启备用泵 |  | When the pump is started, the turning part is encountered 启泵时碰到转到部件 |  | Mechanical damage 机械伤害 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 3 |  | Switch pump 切泵 |  | When the pump is switch, the pump is holding back pressure 切泵时机泵憋压 |  | Damaged pump 机泵损坏 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 4 |  | Stop the original operation pump 停原运行泵 |  | The flow of the pump is interrupted or fluctuates greatly when the original operation is stopped 停原运行泵流量中断或波动较大 |  | Affect the stable operation of subsequent devices 影响后续装置稳定运行 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the executable control measures that need to be added from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要增加的可执行控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety instructions: 安全告知： I have been informed of the hidden hazard source and harmful factors during the operation process, the corresponding safety measures and emergency evacuation methods. 我已经了解本项作业过程中的危险源、危害因素、相应的安全措施和应急疏散的途径。 Signature for confirmation: 签字确认： |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Hazard Analysis (JHA) Record Form 工作危害分析法 （JHA）记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Record No. |  | HYBN-T7-08-2002-2024-2 |  |  |  |  |  |  |  |  |  | Page 2 of 4 |  |  |  |  |
| No. 编号: | 5111-2-004 |  | Department 部门: |  | Utilities Department 公用工程部 |  | Unit 装置: |  | Second Circulating Water 二循环水场 |  |  |  |  |  | Analysis date： 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Task 工作任务: |  |  | Manual backwash side filter 手动反洗旁滤过滤器 |  | Members of analysis group 分析小组成员: |  | Zhang Haoran, Yu Yapeng, Deng Wentao, Zhang Yunbo, Chen Liao, Liangbing、Zhang Feipeng, Zhang Wenjun, Zhao Yu and team members 张浩然、于亚鹏、邓文涛、张云波、梁斌、陈聊、张飞鹏、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Reviewed by 审核人： | Wen Jiancheng, 温建成 |  |  |  |
| S/N 序号 |  | Operation steps 工作步骤 |  | Hazard source or potential incident 危险源或潜在事件 |  | Major accident consequences 主要事故后果 |  | Former occurrence frequency 以往发生频率 |  | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 1 |  | Switch to manual 切手动 |  | Bypass filter is not switched to "manual" mode 旁滤器未切到“手动”状态 |  | Backwash cannot be performed 反洗无法进行 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 2 |  | Operate the valve on site 现场操作阀门 |  | Wrong valve 阀门开错 |  | Poor running water or backwashing effect 跑水或反洗效果差 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 3 |  | Bypass filter backwash 旁滤器反洗 |  | Insufficient or too long backwash time 反洗时间不足或过长 |  | High turbidity 浊度偏高 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  |  |  |  | Sinkhole 污水池冒池 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 4 |  | Restore automatic control 恢复自动控制 |  | After manual backwashing is not switched back to automatic control 手动反洗完未切回自动控制 |  | Automatic backwashing cannot be achieved 自动反洗无法实现 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the executable control measures that need to be added from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要增加的可执行控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety instructions: 安全告知： I have been informed of the hidden hazard source and harmful factors during the operation process, the corresponding safety measures and emergency evacuation methods. 我已经了解本项作业过程中的危险源、危害因素、相应的安全措施和应急疏散的途径。 Signature for confirmation: 签字确认： |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Hazard Analysis (JHA) Record Form 工作危害分析法 （JHA）记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Record No. |  | HYBN-T7-08-2002-2024-2 |  |  |  |  |  |  |  |  | Page 2 of 4 |  |  |  |  |  |
| No. 编号: | 5111-2-005 |  | Department 部门: |  | Utilities Department 公用工程部 |  | Unit 装置: |  | Second Circulating Water 二循环水场 |  |  |  |  | Analysis date： 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |  |
| Task 工作任务: |  |  | Sampling 取样 |  | Members of analysis group 分析小组成员: |  | Zhang Haoran, Yu Yapeng, Deng Wentao, Zhang Yunbo, Chen Liao, Liangbing、Zhang Feipeng, Zhang Wenjun, Zhao Yu and team members 张浩然、于亚鹏、邓文涛、张云波、梁斌、陈聊、张飞鹏、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Reviewed by 审核人： |  | Wen Jiancheng, 温建成 |  |  |
| S/N 序号 |  | Operation steps 工作步骤 |  | Hazard source or potential incident 危险源或潜在事件 |  | Major accident consequences 主要事故后果 |  | Former occurrence frequency 以往发生频率 |  | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 1 |  | Clean the sampling bottle 清洗取样瓶 |  | Take samples without cleaning 取样品未清洗 |  | Analysis erro 分析误差 |  | Occasionally 偶尔 |  | 3 | 2 | 6 | II |  |  |  |  |  |  |
| 2 |  | Collect sampling of water circulation 取样水流通 |  | circulation during sampling for 1-2 minutes 取样时未流通1-2分钟 |  | Data error 数据误差 |  | Occasionally 偶尔 |  | 3 | 2 | 6 | II |  |  |  |  |  |  |
| 3 |  | Sampling 取样 |  | Wrong sample taken during sampling 取样时样品取错 |  | Data error 数据错误 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| 4 |  | Labeling 贴标签 |  | Wrong label 标签贴错 |  | Data error 数据错误 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the executable control measures that need to be added from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要增加的可执行控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety instructions: 安全告知： I have been informed of the hidden hazard source and harmful factors during the operation process, the corresponding safety measures and emergency evacuation methods. 我已经了解本项作业过程中的危险源、危害因素、相应的安全措施和应急疏散的途径。 Signature for confirmation: 签字确认： |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Job Hazard Analysis (JHA) Record Form 工作危害分析法 （JHA）记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Record No. |  | HYBN-T7-08-2002-2024-2 |  |  |  |  |  |  |  |  |  | Page 2 of 4 |  |  |  |  |  |
| No. 编号: | 5111-2-006 |  | Department 部门: |  | Utilities Department 公用工程部 |  | Unit 装置: |  | Second Circulating Water 二循环水场 |  |  |  |  |  | Analysis date： 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |  |
| Task 工作任务: |  |  | Change the lubricating oil 更换润滑油 |  | Members of analysis group 分析小组成员: |  | Zhang Haoran, Yu Yapeng, Deng Wentao, Zhang Yunbo, Chen Liao, Liangbing、Zhang Feipeng, Zhang Wenjun, Zhao Yu and team members 张浩然、于亚鹏、邓文涛、张云波、梁斌、陈聊、张飞鹏、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Reviewed by 审核人： |  |  | Wen Jiancheng, 温建成 |  |  |
| S/N 序号 |  | Operation steps 工作步骤 |  | Hazard source or potential incident 危险源或潜在事件 |  | Major accident consequences 主要事故后果 |  | Former occurrence frequency 以往发生频率 |  | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S |  | R | Level等级 |
| 1 |  | Stop pump and put to manua 停泵后打手动 |  | Replace the lubricating oil without stopping the pump 更换润滑油未停泵 |  | Damaged pump 机泵损坏 |  | Rarely happens 很少发生 |  | 2 | 4 | 8 | II |  |  |  |  |  |  |  |
| 2 |  | Drain the original lubricating oil 放空原润滑油 |  | Waste lubricating oil is dumped at will 废润滑油随意倾倒 |  | Polluted environment 污染环境 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |  |
| 3 |  | Add 加注 |  | Wrong lubricating oil or improper oil level 润滑油加错或油位不合适 |  | Damaged pump 机泵损坏 |  | Rarely happens 很少发生 |  | 2 | 3 | 6 | II |  |  |  |  |  |  |  |
| 4 |  | Resume and clean the site 恢复清理现场 |  | On-site lubricating oil is not cleaned 现场润滑油未清理 |  | Polluted environment 污染环境 |  | Occasionally 偶尔 |  | 3 | 2 | 6 | II |  |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the executable control measures that need to be added from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要增加的可执行控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Safety instructions: 安全告知： I have been informed of the hidden hazard source and harmful factors during the operation process, the corresponding safety measures and emergency evacuation methods. 我已经了解本项作业过程中的危险源、危害因素、相应的安全措施和应急疏散的途径。 Signature for confirmation: 签字确认： |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |