|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5602-001 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Refrigeration station in front of the plant 单元（区域）/工艺过程名称：厂前区制冷站 |  |  |  | Unit/equipment/facility:P001A/B/C/D chilled water pump motor 装置/设备/设施：P001A/B/C/D冷冻水泵电机 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 001 | P001A/B/C/D Chilled water pump running motor inspection P001A/B/C/D 冷冻水泵运行电机检查 |  | Whether the grease of the motor bearing overflows, fill the record 电机轴承润滑脂是否溢出，加注记录 |  | Motor bearing burnt 电机轴承烧 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Whether the motor temperature and current meet the requirements 电机温度，电流是否符合要求 |  | Overload, motor burns 超负荷，电机烧 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the motor meets the requirements 电机振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the noise of the motor has increased 电机杂声是否增大 |  | Motor shaft 电机抱轴 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5602-002 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Refrigeration station in front of the plant 单元（区域）/工艺过程名称：厂前区制冷站 |  |  |  | Unit/equipment/facility:P001A/B/C/D chilled water pump 装置/设备/设施：P001A/B/C/D冷冻水泵 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 002 | P001A/B/C/D chilled water pump running machine pump inspection P001A/B/C/D冷冻水泵运行机泵检查 |  | Whether the lubricating grease of the machine pump bearing overflows, fill the record 机泵轴承润滑脂是否溢出，加注记录 |  | Bearing wear and burnout 轴承磨损、烧坏 | Rarely happens 很少发生 | 2 | 4 | 8 | II |  |  |  |  |  |  |
|  |  |  | Whether the temperature of the pump bearing meets the requirements 机泵轴承温度是否符合要求 |  | Bearing damage 轴承损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the pump meets the requirements 机泵振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the outlet pressure of the pump is normal 机泵出口压力是否正常 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the machine seal is leaking 机封有无泄漏 |  | Damaged mechanical seal 机封损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5602-003 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Refrigeration station in front of the plant 单元（区域）/工艺过程名称：厂前区制冷站 |  |  |  | Unit/equipment/facility:WCH-001A/B/C/D hot water type lithium bromide absorption chiller 装置/设备/设施：WCH-001A/B/C/D热水型溴化锂吸收式制冷机 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 003 | WCH-001A/B/C/D Hot water type lithium bromide absorption chiller WCH-001A/B/C/D 热水型溴化锂吸收式制冷机 |  | Is the hot water temperature of the refrigerator normal 制冷机热水温度是否正常 |  | Affect the concentration of refrigerant 影响冷剂的浓度 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the cold water temperature of the refrigerator is normal 制冷机冷水温度是否正常 |  | Affect the temperature of chilled water 影响冷冻水的温度 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the vacuum of the refrigerator suitable 制冷机真空度是否合适 |  | Affect the efficiency of the refrigerator 影响制冷机的效率 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

|  |  | Hengyi Industries Sdn Bhd 恒逸实业（文莱）有限公司 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Safety Checklist (SCL) Record Form 安全检查表（SCL）分析记录表 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Record No. |  | HYBN-T7-08-2003-2024-2 |  |  |  |  |  |  |  | Page 2 of 2 |  |  |  |  |
| No.: 编号：5602-004 |  | Unit:Utilities Department 单位：公用工程部 |  | Members of SCL analysis group:Zhang Haoran, Yu Yapeng, Zhang Yunbo, Deng Wentao, Liangbing、Zhang Feipeng, Chen Liao, Zhang Wenjun, Zhao Yu And team members SCL分析小组人员：张浩然、于亚鹏、张云波、邓文涛、梁斌、张飞鹏、陈聊、张文俊、赵宇及班组成员 |  |  |  |  |  |  |  | Analysis date: 02 10, 2025 分析日期：2025年2月10日 |  |  |  |  |
| Name of unit (area)/process flow:Refrigeration station in front of the plant 单元（区域）/工艺过程名称：厂前区制冷站 |  |  |  | Unit/equipment/facility:T-001Constant pressure water supplement device 装置/设备/设施：T-001定压补水装置 |  |  |  |  |  |  |  | Reviewed by:Wen Jiancheng 审核人：温建成 |  |  |  |  |
| S/N 序号 | Inspection item 检查项目 |  | Inspection standard 检查标准 |  | Major accident consequences 主要事故后果 | Former occurrence frequency 以往发生频率 | Initial risk assessment 初始风险评价 |  |  |  | Measures to reduce and control risk 风险削减及控制措施 |  | Residual risk assessment 剩余风险评价 |  |  |  |
|  |  |  |  |  |  |  | L | S | R | Level等级 |  |  | L | S | R | Level等级 |
| 004 | T-001 Constant pressure water supplement device inspection T-001 定压补水装置检查 |  | Whether the liquid level of the water tank is normal 水箱液位是否正常 |  | Low pressure in chilled water network 冷冻水管网压力低 | Occasionally 偶尔 | 3 | 2 | 6 | II |  |  |  |  |  |  |
|  |  |  | Is the outlet pressure of the constant pressure make-up pump normal 定压补水泵出口压力是否正常 |  | Low or high pipe network pressure 管网压力低或高 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the vibration value of the motor meets the requirements 电机振动值是否符合要求 |  | Equipment damage 设备损坏 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
|  |  |  | Whether the noise of the motor has increased 电机杂声是否增大 |  | Motor shaft 电机抱轴 | Rarely happens 很少发生 | 2 | 3 | 6 | II |  |  |  |  |  |  |
| Descriptions: 说明： 1. For occurrence frequency, consider how many cases of such hazard have happened on similar equipment of the same industry. 发生频率考虑同行业类似装置设备发生该类危险的案例多少。 2. The initial risk assessment examines situations where there are no controls for the risk, including extreme situations that may occur. 初始风险评价考虑该风险无任何控制措施的情形，包括可能发生的极端情况。 3. Risk reduction and control measures Fill in the control measures that need to be maintained or increased from the aspects of personnel ability and quality, operating procedures, operation plans, safety facilities, inspection and monitoring, hidden danger management, and emergency plans. 风险削减及控制措施填写需要保持或增加的控制措施，从人员能力和素质、操作规程、作业方案、安全设施、检查监测、隐患治理、应急预案等方面考虑。 4. Filling of residual risk assessment adopts the risk assessment results after risk reduction and control measures. 剩余风险评价填写采取风险消减及控制措施后的风险评价结果。 Medium and high risk lists shall be filled based on the results of initial risk assessment. 5. 中高度风险清单的填写以初始风险评价结果为准。 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |