## 日检表 (28)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期：11 MM 19 DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分技改线加保温,加氢保温恢复
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 盲板隔离
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 提问员工回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态

## 月检表 (27)
HSE Monthly Checklist for No.2 Refining Department 炼油二部HSE月检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.2 Risk management 风险管理 | 5.2.1.4 Organize hazard identification and risk assessment of in-service equipment and facilities at least once a year; 每年应至少组织一次对在役设备设施的危险源辨识与风险评价； 5.2.1.5 Organize hazard identification and risk assessment of various work in normal production at least once a year; 每年应至少组织一次正常生产过程中各项作业活动的危险源辨识与风险评价； 5.2.1.9 In production and other relevant activities, all departments and their staff shall conduct hazard identification and risk assessment and control as per the specified time, period and method and be responsible for the results. 各部门及员工在从事生产作业和其它相关活动时，应按规定时间、周期、方法进行危险源辨识、风险评价和控制，并对其结果负责。 5.2.1.10 Each department shall sort out its own operation activities, equipment and facilities,and submit the list of operation activities and equipment of the department to the competent business department for review. 各部门梳理本部门作业活动与设备设施，报业务主管部门审核后形成本部门的作业活动清单与设备清单。 5.2.4.1 For identified risks, each department shall expressly define and establish the responsibility, scope, methods and requirements related to the risk management & control, and shall integrate the safety risk control and hidden hazard screening into the management of production process, and ensure the risks are under control through hazard identification, risk assessment, risk control and monitoring. 对于辨识出的风险，各部门应明确风险管理的职责、范围、方法及风险管控要求等，将安全风险管控和隐患排查治理融入生产过程管理工作，通过危害辨识、风险评估、风险控制及风险监控，保证风险处于受控状态。 5.2.4.2 All departments need to take immediate measures to control the huge risks assessed. Major risks require immediate or near-term management; Moderate risk management within 2 years. Governance should be in the order of elimination and replacement,engineering control, management measures, individual protection to choose governance measures. 各部门对于评价出的巨大风险，需要立刻采取措施治理；重大风险需要立即或近期治理；中等风险在 2 年内治理。治理应按照消除、替换、工程控制、管理措施、个体防护的顺序来选择治理措施。 | Whether the hazard identification and risk assessment are carried out on time 是否按时进行危险源辨识与风险评价 | 已按公司要求完成，并根据公司要求更改，打印放到外操室和中控室，并提问
|  |  | Whether to organize full-staff learning 是否组织全员学习 | 已在副班时组织学习
|  |  | Are the identified risks effectively managed 是否有效管控辨识出的风险 | 根据现场作业情况做好风险辨识
加氢保温,气分技改线保温, A203雨棚焊接施工
本月加裂查找隐患登记31项，加氢8项
| HSE Comprehensive Management System HSE 综合管理制度 5.14 HSE assessment HSE 考核 | 5.14.2 Each department shall refer to the Company's "Performance Appraisal Measures" or refine the performance appraisal system of its own department to assess, reward and punish the HSE work of its own department, and establish the HSE assessment reward and punishment ledger. 各部门引用公司《绩效考核办法》或细化为本部门绩效考核制度，对本部门的 HSE 工作情况进行考核奖惩，并建立 HSE 考核奖惩台帐。 | Whether to transform and compile the HSE assessment system of the department 是否转化编制部门HSE考核制度 | 已按要求做好日周月检更新
|  |  | Whether to conduct assessment on violations of HSE regulations within the department 是否对部门内违反HSE制度的行为进行考核 | 有日周月检已囊括所有制度内容，并不断更新
|  |  | Have you established a record of HSE assessment rewards and punishments 是否建立HSE考核奖惩台账 | 已建立
| HSE Comprehensive Management System HSE 综合管理制度 5.15 Emergency Preparedness and Response 应急准备与响应 | 5.15.5.3 Emergency plans shall be revised once three years and such revision shall be recorded and filed. 预案至少每三年修订一次，预案修订情况应有记录、归档并备案。 5.15.6.1 Each department should train employees on emergency regulations, emergency plans, emergency skills, accident cases and other emergency nowledge, and record them in training files. When the emergency plan involves contractors, the contractors should be trained. 各部门应对员工进行应急法规、应急预案、应急技能、事故案例等应急知识进行培训，并在培训档案中进行记录，应急预案涉及承包商时，应对承包商实施培训。 5.15.6.2（2）As for onsite disposal plan, operation department shall exercise such plan at least once a month for each shift, including one onsite actual emergency exercise. 现场处置预案运行部每班每月演练不少于 1 次，其中必须包括 1 次现场实战应急演练。 5.15.6.6 At the end of exercise, all departments shall immediately complete Emergency Exercise Record. 各部门演练结束后，应及时填写《应急演练记录》。 | Whether it is revised in time 是否及时修订 | 公司已修订
|  |  | Whether relevant training is carried out 是否进行相关培训 | 已完成培训，培训进度副班学习内容可查
|  |  | Whether the drill is conducted as required 是否按要求进行演练 | 本月已完成8个班组演练
Comprehensive Management 综合管理 | 5.5 Compliance management 合规管理 | 5.5.3.1 All functional departments shall obtain HSE laws, regulations and other related requirements concerning all production & operation links of the Company from competent government departments and superior company in a timely manner. 各职能部门从政府主管部门和上级公司及时获取与公司生产经营各环节相关的HSE法律法规及其他有关要求。 | Is it carried out as required? 是否按要求开展 | 已按公司发布要求开展
|  | 5.5.3.2 All functional departments shall update and submit list of HSE laws, regulations and other related requirements applicable to themselves to HSE Dept. within one week prior to the end of half a year. 各职能部门应在每半年结束前1周内更新并向HSE管理部报送本部门适用的HSE法律法规及其他有关要求清单。 | Is it carried out as required? 是否按要求开展 | 已按公司发布要求开展
|  | 5.5.3.3 All functional departments shall identify and obtain HSE laws, regulations and other related requirements and communicate them to all related parties. 各职能部门应将识别、获取的HSE法律法规及其他有关要求传达到各相关方。 | Is it carried out as required? 是否按要求开展 | 已按公司发布要求开展
|  | 5.5.4.1 All functional departments shall include HSE laws, regulations and other related requirements into management systems related to their disciplines. 各职能部门应当将HSE法律法规及其他有关要求纳入到本专业相关管理制度中。 | Is it carried out as required? 是否按要求开展 | 已按公司发布要求开展
|  | 5.5.4.2 All departments shall implement HSE laws, regulations and other related requirements in a strict manner. 各部门应严格执行HSE法律法规及其他有关要求。 | Whether employees can obtain company notifications and department management systems in a timely manner 员工是否能及时获取公司通知与部门管理制度 | 公司及部门网站可查询
| 5.6.4 Ready for startup or commissioning 开车或投用前准备 | 5.6.4.2 Pre-Startup Safety Review applies to all HengYi existing production plants and new plants. Pre-startup safety review needs to be done for new plant completed before commissioning and for plant transformation project (including Major MOC) and overhaul before re-startup. PSSR开车前安全审查适用于恒逸所有现有生产装置和新建装置。新建项目完成后的投用、装置改造项目（含重大MOC）以及大检修后重新开车之前，需要进行开车前安全审查。 | Whether a pre-startup safety review has been conducted after maintenance or new construction of the unit 检修开工或新建装置是否进行了开车前安全审查 | 已按要求做好开车前检查，记录可查
Comprehensive Management 综合管理 | 5.7 Management of safety production information facilities 安全生产信息管理 | 5.7.1 Each department of the company shall collect and maintain HSE related information within its business scope, and ensure that relevant personnel (including contractor personnel) obtain the latest HSE information in a timely manner, so as to match the post risk control requirements. 公司各部门应收集、维护本部门业务范围内与HSE相关的信息，保证相关人员（包括承包商人员）及时获取最新的HSE信息，使其与岗位控制风险需求相匹配。 | Safety technical instructions and other production safety information collected by this department 本部门收集的安全技术说明书等安全生产信息 | 安全技能说明书齐全
| 5.8 Management of HSE facilities HSE设施管理 | 5.8.2.3 All departments shall conduct regular inspection of safety facilities and those required verification shall be verified by all competent departments periodically. 各部门应对安全设施定期检查，需校验的安全设施由各主管部门定期校验。 | Regular calibration of various instruments 各类仪表定期校验 | 已按要求做好检查
Change Management 变更管理 | 5.1 Change request 变更申请 | 5.1.1 The applicant shall designate a special person to be responsible for a change management work, and the person in charge shall initiate the change application. 申请单位应指定专人负责某一项变更管理工作，由负责人发起变更申请。 | Verify that a designated person is assigned to manage the change process and that they have initiated the change application. 确认已指派专人来管理变更流程并且该已发起线上变更申请。 | 谁发起谁负责变更，变更清单按要求更新
|  | 5.1.3 After the change department organizes the change risk assessment and implements the control measures, the person in charge shall initiate the online change application process, submit the change application to the competent department, and attach the change risk assessment and control measures results. 变更部门组织进行变更风险评估并落实管控措施后，由负责人发起在线变更申请流程，向主管部门提出变更申请，并附带变更风险评估及管控措施。 | Submitted the application with supporting documents. 提交申请并附上相关文件。 | 已按要求执行
| 5.2 Risk assessment 风险评估 | 5.2.1 The risk of change includes the risk during the implementation of change and the risk after the implementation of change. 变更的风险包括变更实施过程中的风险和变更实施后的风险。 5.2.2 All departments shall identify and evaluate the potential risks of changes before applying for changes. 各部门申请变更前应对变更的潜在风险进行辨识和评估。 | Check whether risk identification and assessment have been carried out and relevant forms have been formed 检查是否开展风险辨识和评估，并形成相关表格 | 变更工作已按要求完成
|  | 5.2.5 The risk assessment team members should have certain risk assessment ability and work experience, including but not limited to safety, process, equipment, operation, electrical equipment, design and other personnel to participate, to ensure that the change risk is fully identified and effective risk control measures are developed. 进行风险评估的团队成员应具备一定风险评估能力和工作经验，包括但不限于安全、工艺、设备、操作、电仪、设计等人员参加，确保充分识别变更风险，制定有效风险控制措施。 | Check if team members is made up of the right person to attend 检查团队成员是否由合适的人员组成 | 人员符合
| 5.3 Alteration process 变更审批 | 5.3.3 After the change risk assessment is approved, it shall be countersigned by the centralized management department and other departments involved. 变更风险评估审批通过后，由归口管理部门及其他所涉及的部门进行会签。 5.3.4 General changes are reviewed by relevant functional departments and approved by company leaders. 一般变更由相关职能部门进行审核，公司领导进行批准。 5.3.5 The SafetyCase shall be updated according to the requirements of the government, and shall be implemented after examination and approval by the competent government department. 重大变更按政府要求，更新 SafetyCase，并经政府主管部门审核批准后实施。 | Check if risk assessment approval process includes countersigning by relevant departments, and if change level follows the relevant requirement 检查风险评估审批流程是否包括相关部门的会签，变更级别是否符合相关要求 | 符合
| 5.4 Alteration implementation 变更实施 | 5.4.4 In the process of change implementation, if there may be a large security risk, emergency plans should be prepared in advance, and the preparation of various emergency measures should be implemented. 变更实施过程中，如可能产生较大的安全风险，应提前编制应急预案，并在实施中落实各项应急措施的准备情况。 | Check if emergency plans are prepared for high-risk changes. 检查是否针对高风险变化准备好了应急预案。 | 已有配套预案
| 5.6 Acceptance of changes 变更的验收 | 5.6.1 After the implementation of the change, the centralized management department shall organize relevant departments to carry out the acceptance of the change. Acceptance includes an assessment of the conformity of the change with the intended effect. The acceptance work shall not exceed 90 days after the change is put into use. After acceptance,fill in the Change Acceptance Form. 变更实施结束后，由归口管理部门组织相关部门对变更进行验收工作。 验收包括对变更与预期 效果符合性的评估。验收工作不应超过变更投用后 90 天。 验收后填写《变更验收表》。 | Check if post-implementation acceptance is completed within 90 days and documented. 检查实施后验收是否在90天内完成并记录。 | 符合要求
| 5.7 The application of the change 变更的投用 | 5.7.1 The change department shall conduct beneficiary training and inform the personnel who may be affected by the change, including the purpose, function, content and operation methods of the change, possible risks and impacts in the change, risk control measures, and similar accident cases. 变更部门应对变更可能受影响的人员进行受益人培训和告知，培训内容包括变更目的、作用、变更内容及操作方法、变更中可能的风险和影响、风险的管控措施、同类事故案例等。 | Check if training is conducted for affected personnel on changes, risks, and controls. 检查是否对受影响的人员进行了有关变化、风险和控制的培训。 | 培训记录建全
|  |  | 环境班XXXX离职后，XXXX转副班长岗位，未提供转岗培训记录。 抽查XXX员工培训档案，2024年再培训时长不符合公司制度要求 | 人员转岗及时建立档案，本月一人转岗到我们部门。
| 5.8 Acceptance and closure 变更关闭 | 5.8.1 After the implementation of the change, the change department shall timely update the PID drawings, operating procedures, risk assessment, interlocking logic diagrams and other documents involved in the change, and archive the records involved in the change process. 变更实施后，变更部门应及时更新变更涉及的 PID 图纸、操作规程、 风险评价、 联锁逻辑图等文件资料，并将变更过程涉及的记录资料归档。 归口管理部门建立本专业管理台帐。 | Check if P&ID drawings, procedures, risk assessments, and interlocking logic diagrams are up to date, and if it is shared to operators 检查P&ID图纸、程序、风险评估和联锁逻辑图是否是最新的，以及是否与下发给班组 | 已及时更新
|  | 5.8.2 Change management files shall at least include change application approval form, risk assessment record, change acceptance record, change closure confirmation record and other documents related to change. 变更管理档案至少应包括变更申请审批表、风险评估记录、变更验收记录，变更关闭确认记录和与变更相关的其他文件资料等。 | Check if all required documents related to change management are proper documented 检查与变更管理相关的所有必需文件是否已正确保存、归档 | 已保存归档
| 5.10 Emergency change 紧急变更 | 5.10.3 The emergency change shall be implemented after the on-site person in charge confirms the implementation of risk control measures. Relevant records shall be made during the implementation period, and the change procedures shall be completed within 48h after the implementation according to the change procedure. 紧急变更经现场负责人确认落实风险管控措施后实施，实施期间应做好相关记录，在实施后48h内按变更流程补办变更手续。 | Confirm that emergency changes are properly documented and procedures completed within 48 hours. 确认紧急变更已正确记录并且程序已在48小时内完成。 | 已按要求执行
Occupational Health Management 职业卫生 | Identification and assessment of occupational hazard factors 职业病危害因素识别与评估 | 5.2.2 The department’s evaluation team members must reviewed the task activity list, discuss each task activity and work step in detail to conduct an Health Risk Assessment. The identification results shall be recorded in the “HYBN-T7-08-4006-2024-1 Health Risk Assessment (HRA) Record Form”. 各部门评价小组成员按照作业活动清单，对每项作业活动和作业步骤逐项讨论，进行职业病危害风险评估，辨识结果列入《HYBN-T7-08-4006-2024-1职业健康危害因素评估分析 （HRA）记录表》。 | Operational Activities and Steps: Ensure all operational activities and steps are identified and discussed item by item with the evaluation team members according to the checklist. 作业活动及步骤: 确保所有作业活动和作业步骤均被识别，并按清单逐项与评价小组成员讨论 | 符合要求
|  |  | Identification of Occupational Disease Hazard Factors: 1. Identify potential occupational disease hazards, including chemical, physical, biological, ergonomic, and psychological factors. 2. Assess the likelihood of hazards based on workplace environment, operational methods, and exposure duration. 职业病危害因素辨识： 1.识别可能存在的化学、物理、生物、人体工学及心理因素等职业病危害。 2.结合作业环境、操作方式、接触时间等因素，确认危害的可能性。 | 符合要求
|  |  | Risk Assessment: 1. Evaluate the risk level of occupational disease hazards using risk assessment methods (e.g., severity of hazard, exposure frequency, and duration). 2. Record the current hazard control status for each operational step and analyze whether further improvements are needed. 风险评估 1.依据风险评估方法（如危害严重程度、暴露频率、接触时间等），评估职业病危害风险等级。 2.记录各作业步骤的危害控制现状，并分析是否需进一步改进。 | 符合要求
|  |  | Inspection of Control Measures: 1.Determine the effectiveness of existing protective measures (engineering, administrative, and personal protective equipment). 2.Verify compliance with occupational health management systems and emergency response plans. 控制措施检查 1.现有防护措施（工程、行政、个体防护）是否有效。 2.是否有合规的职业健康管理制度和应急预案。 | 符合要求
|  |  | Records and Documentation: 1. Ensure that hazard identification results and assessment data are fully recorded in the “HYBN-T7-08-4006-2024-1 Occupational Health Hazard Assessment (HRA) Record Form.” 2. Ensure the record form is properly filled out with accurate data for future review and improvement. 记录与归档 1.确保辨识结果和评估数据完整记录在《HYBN-T7-08-4006-2024-1 职业健康危害因素评估分析（HRA）记录表》。 2.确保记录表填写规范，数据准确，以便后续审查和改进。 | 符合要求
| Management of occupational hazards 职业病危害因素管理 | 5.3.1 Quality Analysis Department is responsible for monitoring occupational disease hazards and inputting the data into LIMS system. 质量检验部负责职业病危害因素监测，检测、评价结果录入LIMS系统。 | Confirm whether monitoring is conducted according to the 2025 Occupational Health Monitoring Points and whether the evaluation results are entered into the LIMS system on time. 是否按照2025年职业健康监测点进行监测并按时把评价结果录入LIMS系统。 | 已按要求执行
|  | 5.3.4.2 Each execution department shall notify employees the monitoring results of occupational disease hazards of the work they are engaging in by using monitoring bulletin boards. 各执行部门HSE专业以监测告示牌的方式向员工告知本岗位职业病危害因素监测结果。 | Check if occupational hazard monitoring results are publicly posted at the workplace. 检查现场是否有公告职业危害因素监测结果 | 外操室外墙上已张挂
|  | 5.3.4.3 Monitoring results of occupational hazard results (i.e. Quality Inspection Report) shall be published in the Occupational Health notice board and updated within 5 working days. 职业病危害因素监测结果（质检报告单）应在职业健康公告栏展示并在5个工作日内完成更新 | Ask the employees if they know where to check the occupational hazard monitoring results. Do they know when the results will be available? If the data exceeds the limit, will it be communicated during the pre-shift meeting, and will employees be reminded to take protective measures? 询问员工是否知道哪里查职业危害因素监测结果？是否知道什么时候结果出来？数据超标是否班前会进行宣贯并提醒员工做好防护措施？ | 抽查提问朱树成，苟薄，韩德锋，汪兵强，王庆昆，穆尼尔，回答良好。
|  | 5.3.7.1 Warning signboards with Chinese and English warning instructions must be place where there may be serious occupational disease hazards. 在可能产生严重职业病危害作业岗位的醒目位置,设置警示标识和中、英文警示说明。 | Ensure warning signs are in place for areas with potential over-limit exposure. 现场有可能超标的地点是否有相关的警示标识 | 现场标识张挂齐全
|  | 5.3.7.4 When signing labor contracts with employees, the HR Dept. shall truthfully inform employees of the occupational hazards that may arise in the work position process and its consequences, occupational disease prevention measures, etc., and state clearly in the labor contracts. 人力资源部在与员工签订劳动合同时，应当将工作岗位过程中可能产生的职业病危害及其后果、职业病防护措施等如实告知员工，并在劳动合同中写明 | Confirm that the department has proper record-keeping procedures. 部门是否做好归档？ | 部门不涉及
|  | 5.6.3.1 Operation protection 作业防护 （4）Operators must check the condition of the gas mask filters before using and department safety engineer must regularly check on the validity of the gas mask filters. 员工必须在使用滤毒盒前检查滤毒盒的状况，部门安全工程师必须定期检查过滤器的有效性 | Are employees aware of when to replace gas filter cartridges and how to conduct a face seal check on masks? Are managers conducting regular inspections of gas filter cartridge validity in gas cabinet? 员工是否知道什么时候更换滤毒盒，是否知道怎么对口罩进行气密性检查？管理人员是定期检查气防柜的滤毒盒的有效期？ Check expiry of gas filters, gas mask in emergency cabinet 检查紧急柜中的气体滤毒盒和防毒面具的有效期 | 滤毒盒没过期，员工知晓如何检查
|  | 5.6.4 Dust protection 粉尘防护 5.6.5 High temperature protection 高温防护 5.6.6 Acid and alkali protection 酸碱防护 | Are employees aware of which PPE is required for different toxic and hazardous work environments? Do employees understand the potential health effects of these toxic and hazardous gases? 对各种有毒有害工作环境，是否知道是用什么劳动防护用品进行防护？ 询问员工是否知道这些有毒有害气体对人员会造成什么伤害？ | 抽查提问朱树成，苟薄，韩德锋，汪兵强，王庆昆，穆尼尔，回答良好。
|  | 5.6.7.2 All personnel engaged in radiation-related work are required to wear a personal radiation dosimeter (RPL) as specified. The RPL must be measured monthly to ensure that the annual radiation dose does not exceed 20 mSv. 凡从事辐射相关工作人员，按要求佩戴个人辐射剂量计（简称RPL） 每月对RPL进行计量检测，确保年辐射剂量不超过20mSv。 | Ensure radiation-exposed personnel wear RPL (Radiation Personal Dosimeter) when working in radiation environments. 检查辐射人员接触辐射工作环境时是否佩戴RPL | 本月无射线作业
|  | 5.6.7.3 Departments involved in radiation-related work should equip radiation protective suits and related materials in the gas cabinet. 凡设计从事辐射相关工作的部门应在气防柜内配置辐射防护服相关物资。 | Verify whether the relevant departments are properly equipped with radiation safety measures. 相关部门是否配备？ | 无配备
| Occupational Health Archive 职业健康档案 | Departments shall establish OH Archives, and fill in the requisition and issuance in the accounts; 部门应建立本部门员工个人职业健康档案 | Whether department establish OH archive for employees and update annually 是否建立员工职业健康体检档案并一年一更新 | 已建立并及时更新
|  | 5.3.4.4 Monitoring results of occupational hazard results shall be recorded in the Occupational Health archives and updated once every year. 职业病危害因素监测结果应存档入职业健康档案并每年更新一次。 | Has an occupational health examination file been established for employees? Are health records updated regularly? Are health records established for new employees? Are on-the-job medical examination results updated in the records? Radiation personnel medical records updated yearly in OH archive? 是否建立员工职业健康体检档案 是否档案有滚动更新 检查新人是否建立健康档案 在岗体检结果是否更新在档案里 辐射岗位人员体检结果是否有更新到档案里？ | 档案已建立
|  | Departments must regularly update employee's medical check-up information into the OH archives 部门应定期更新职业健康体检信息 | Whether department update OH medical information regularly 是否定期更新员工职业健康体检信息 | 已按人员回国情况做好体检更新
| Work Injury Management 工伤管理 | Recognition of Work Injuries工伤认定 （1）In the event of a work-related injury or an occupational disease, the company representative shall complete the “Work Injury Identification Application Form” and submit it within 30 days. 员工发生工伤或罹患职业病，公司代理人填写《工伤认定申请表》在30天内提出申报; | Is the “Work Injury Identification Application Form” completed by the company representative after an employee sustains a work injury or is diagnosed with an occupational disease? Is the application submitted within the required 30-day period? Are the relevant records and submission documents complete, properly formatted, and archived for future reference? 是否在员工发生工伤或确诊职业病后，由公司代理人填写《工伤认定申请表》？申请是否在规定的30天内提交？相关记录和申报材料是否完整、规范，并存档备查？ | 未发生工伤
| Management on atmospheric pollution 大气污染管理 | 5.4.2.1 (1) Develop waste gas control and emission indicators and relevant operation specifications. 制定废气控制排放指标与相关操作规程。 | Whether to formulate the department's exhaust gas management system (operating procedures for abnormal working conditions) 是否制定本部门废气管理制度（异常工况操作规程） | 部门不存在废气排放
|  | 5.4.2.1(2) Optimize the production process and operation management to ensure the up-to-standard discharge of all types of waste gas. 优化生产工艺与操作管理，确保各类废气达标排放标准。 | 1. Check the LIMS waste gas emission monitoring data to see if the atmospheric pollutant emission data meets the standards. 2. If the waste gas emission exceeds the standard, analyze the reasons for exceeding the standard and optimize and improve the production process and operation management. 1.查LIMS废气排放监测数据，大气污染物排放数据是否达标。 2.废气排放超标是否分析超标原因，是否对生产工艺与操作管理进行优化和技改。 | 部门不存在废气排放
|  | 5.4.2.2 (3) The purging of the device during startup and shutdown shall be airtight purging, and the waste gas from the purging shall be discharged into the flare system and recovered by the gas cabinet as possible. 装置开工、停工中吹扫采用密闭吹扫，吹扫废气应排往火炬系统，尽量由气柜回收。 | 1. Check the HSE control plan for start-up and shutdown to see whether the plan has formulated requirements for closed purge work. 2. Check the site to see whether the closed purge management requirements for start-up and shutdown plans are strictly implemented. 1.查开停工HSE管控方案，方案是否制定密闭吹扫工作要求。 2.查现场，是否严格落实开、停工方案密闭吹扫管理要求。 | 已按要求执行
|  | 5.4.2.1(7) In case of any failure of the waste gas treatment facilities and monitoring facilities, the de-partment in charge of which shall timely repair them and put into use according to the proce-dures and report to the HSE Dept. 废气处理设施、监测设施出现故障，所在部门应按程序及时修复投用，并报告HSE管理部。 | 1. Check the report to see if any failure of the exhaust gas treatment facilities and monitoring facilities has been reported to the HSE Management Department. 2. Check the maintenance plan and maintenance records to see if the maintenance plan has been submitted in a timely manner. 1.查报告，废气处理设施、监测设施出现故障是否报告HSE管理部。 2.查维修计划和维修记录，是否及时提报维修计划。 | 部门不存在废气排放
|  | 5.4.2.2 (1) Environmental protection plans shall be formulated for startup and shutdown. Predictions on atmospheric pollutants that may be emitted shall be carried out. Scheme measures to con-trol and reduce atmospheric pollutants shall be taken. And the scheme for startup and shut-down must be reviewed and approved by the relevant departments and leaders. 开停工应制定环保方案，对可能排放的大气污染物进行预测，应有控制与减少大气污染物的方案措施，开、停工方案须经相关部门与领导审批。 | Check the environmental protection plan for the shutdown 1. Whether the plan contains air pollutant control measures. 2. Whether the plan has been approved by relevant departments. 查开停工环保方案 1.方案内容是否制定大气污染物控制措施。 2.方案是否经相关部门审批。 | 已制定
| Noise management 噪声管理 | 5.6.4 The amount of steam purging shall be controlled for shutdown purging of the produc-tion equipment to reduce the noise of steam emptying to pollute the surrounding environment. 生产装置停工吹扫要控制蒸汽吹扫量，减少蒸汽放空的噪声污染周边环境。 | 1. Check the HSE control plan for the shutdown of the device, and whether a purge plan has been formulated for the steam purge and venting of the device, and whether it has been approved by the HSE Management Department. 2. Check the site and monitor whether the noise at the factory boundary exceeds the standard. 1.查装置停工HSE管控方案，装置停工蒸气吹扫放空是否制定吹扫方案，并经HSE管理部审批。 2.查现场，监测厂界噪声是否超标。 | 已制定
|  | 5.6.6 The environmental monitoring station of the Quality Analysis Dept. shall monitor the noise at boundary in accordance with the analysis plan. 质量检验部环境监测站应对厂界噪声按照分析计划进行监测。 | Check LIMS to see whether the Quality Inspection Department has completed the factory boundary noise monitoring according to the annual environmental monitoring plan. 查LIMS，质检部是否按年度环境监测计划完成厂界噪声监测。 | 噪声已按要求检测
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (11) Equipment and pipelines must be equipped with silencing facilities on the purging vent nozzle to prevent the noise from exceeding standard to cause disturbances to residents. 设备、管线吹扫放空口必须加消音设施，杜绝噪声超标扰民事件发生。 | Check the site to see whether the equipment and pipeline purge vents have been equipped with silencer facilities as required. 查现场，设备、管线吹扫放空口是否按要求增加消音设施。 | 消音设施齐全
| Management on environmental protection facilities 环保设施管理 | 5.8.1.2 Environmental protection facilities must be ensured to operate normally. No one may shut down, idle, or dismantle them without authorization. 环境保护设施必须确保正常运转，任何人员不得擅自停运、闲置、拆除。 | Check the site to see whether the environmental protection facilities are operating normally and whether they have been shut down, idled or demolished without permission. 查现场，环保设施是否正常运转，未经许可是否存在停运、闲置和拆除。 | 正常运转
|  | 5.8.1.3 Environmental protection facilities shall be incorporated into the Company’s equip-ment and facilities management. 环保设施纳入公司设备设施管理。 | Check the equipment management ledger and maintenance records to see whether environmental protection facilities are included in the equipment and facility management, and are regularly inspected and maintained. 查设备管理台账和维护记录，是否将环保设施纳入设备设施管理，并定期检查、维护。 | 清污分流正常运转无污染
|  | 5.8.2.1 The environmental protection facilities and on-line automatic monitoring instruments shall operate in strict accordance with the operation specifications, and the operating parame-ters shall meet the design requirements. 环境保护设施、在线自动监控仪表运行严格按照操作规程执行，操作参数符合设计要求。 | 1. Check the operating procedures, whether the environmental protection facilities and online automatic monitoring instruments have formulated operating procedures, and whether the management requirements of "start first and stop later" are implemented. 2. Check the operating parameters and whether the parameter settings are in accordance with the design. 1.查操作规程，环保设施和在线自动监控仪表是否制定操作规程，是否落实先开后停管理要求。 2.查操作参数，参数设置是否符合设计。 | 部门不涉及
|  | 5.8.2.2 The operators of environmental protection facilities and on-line automatic monitoring instruments must be qualified after the job-specific training and obtain the work license be-fore operating. 环境保护设施、在线自动监控仪表运行的操作人员必须经过岗位培训合格，取得上岗证后方可操作。 | Check the operator's job certificate and whether the operators of environmental protection facilities and online automatic monitoring instruments have received job training and obtained certificates before taking up their posts. 查操作人员上岗证书，环境保护设施、在线自动监控仪表运行的操作人员是否经过岗位培训并取证上岗。 | 部门不涉及
|  | 5.8.2.3 In case of any abnormal operation of environmental protection facilities and on-line automatic monitoring instruments, the production and operation department must promptly find out the causes of abnormalities and make adjustment to ensure a qualified pollutant dis-charge, and shall inform the Scheduling & Dispatch Dept. and the HSE Dept. of the causes of abnormalities by mail. 环境保护设施、在线自动监控仪表运行异常，生产运行部门要及时查清异常原因并调整，确保污染物排放合格，对异常原因以邮件形式告知计划调度部、HSE管理部。 | If there are any abnormalities in the operation of environmental protection facilities or online automatic monitoring instruments, please notify the Planning and Coordination Department and the HSE Management Department via email. 环境保护设施、在线自动监控仪表运行异常，是否邮件通知计调部和HSE管理部。 | 部门不涉及
|  | 5.8.2.5 In case of any fault, damage or defect found in the environmental protection facilities and on-line automatic monitoring instruments, the production and operation department shall promptly deal with them. If they cannot be solved, it shall report in time to the HSE Dept. and the Equipment Management Dept. to jointly solve the problem. 生产运行部门发现环境保护设施、在线自动监控仪表存在故障、损坏、缺陷时，及时处理，如无法解决应及时汇报HSE管理部和机械动力部共同解决。 | 1. Whether environmental protection facilities and online automatic monitoring instruments are handled in a timely manner when they are faulty, damaged or defective. 2. Whether environmental protection facilities and online automatic monitoring instruments are reported to the HSE Management Department when they are faulty, damaged or defective. 3. Whether environmental protection facilities and online automatic monitoring instruments are recorded in the environmental protection facility operation management ledger when they are faulty, damaged or defective. 1.环保设施、在线自动监控仪表存在故障、损坏、缺陷时，是否及时处理。 2.环保设施、在线自动监控仪表存在故障、损坏、缺陷时，是否汇报HSE管理部。 3.环保设施、在线自动监控仪表存在故障、损坏、缺陷时，是否在环保设施运行管理台账中记录。 | 清污分流正常运转无污染
|  | 5.8.2.6 In the event that the environmental protection facilities and on-line automatic monitor-ing instruments are scheduled to be shut down for overhaul or comparison monitoring, the shutdown report form shall be submitted to the Scheduling & Dispatch Dept. and the HSE Dept. for review and approval at least 24 hours in advance; unplanned shutdown for overhaul due to sudden events shall be promptly reported to the Scheduling & Dispatch Dept. and the HSE Dept. by telephone. See appendix for the shutdown report form. 环境保护设施、在线自动监测仪表计划停运检修或比对监测，至少提前24h将停运报告表报告计划调度部、HSE管理部审批；因突发性事件停车的非计划停运检修，应及时电话报告计划调度部、HSE管理部。 | 1. Check the comparison report to see whether the online automatic monitoring instrument is compared and monitored according to the annual environmental monitoring plan frequency requirements. 2. During the comparison monitoring period, whether the process is adjusted to be stable and the external emission index monitoring is qualified. 3. Whether the environmental protection facilities are shut down for maintenance and whether they are reported to the HSE Management Department for approval in advance. 1.查比对报告，是否按年度环境监测计划频次要求对在线自动监测仪表进行比对监测。 2.比对监测期间，是否调整工艺至稳定，且满足外排指标监测合格。 3.环保设施停运检修，是否提前报告HSE管理部审批。 4.因突发性事件导致的环保设施非计划停运检修，是否及时电话报告HSE管理部。 | 部门不涉及
|  | 5.8.2.7 The production and operation department shall establish and perfect the manage-ment ledgers of environmental protection facilities and on-line automatic monitoring instru-ments, set obvious name and description marks on the site, and shall not practice falsification on the operating conditions and monitoring data. 生产运行部门应当建立健全环境保护设施、在线自动监控仪表的管理台账，现场要有明显的名称、说明标识，不得对运行工况和监测数据弄虚作假。 | 1. Check the environmental protection facility records to see whether a management record of environmental protection facilities (including online automatic monitoring instruments) has been established. 2. Check the environmental monitoring data to see if there is any data fraud. 1.查环保设施台账，是否建立环保设施（包括在线自动监控仪表）管理台账。 2.查环境监测数据，是否存在数据弄虚作假。 | 含油污水数据及时记录
|  | 5.8.2.8 The production and operation department shall set routing inspection sites to regular-ly conduct routing inspection on environmental protection facilities and on-line automatic mon-itoring instruments, and make routing inspection records. 生产运行部门应当设定巡检站点，定时巡检环境保护设施、在线自动监控仪表，并做好巡检记录。 | 1. Check the site to see if there are inspection points for environmental protection facilities. 2. Check the inspection records to see if environmental protection facilities are inspected on time. 1.查现场，环保设施是否设置巡检点。 2.查巡检记录，环保设施是否按时巡检。 | 含油污水井及水沟在巡检路线内
|  | 5.8.2.9 The production and operation department shall check the data upload of the on-line automatic monitoring instruments once at least every 2 hours per shift. In case of any abnor-mal data transmission, the causes shall be found out and reported to the HSE Dept. by the shift on duty. 生产运行部门每班至少2小时检查一次在线自动监控仪表数据上传情况，数据传输异常时，应查清原因，当班报告HSE管理部。 | 1. Check the system or management requirements to see if the data upload of online automatic monitoring instruments is checked every 2 hours. 2. Set alarms to remind employees when data transmission is abnormal. 3. When data transmission is abnormal, find out the cause and report it to the HSE management department. 1.查制度或管理要求，是否落实每2小时检查一次在线自动监控仪表数据上传情况。 2.数据传输异常是否设置报警提醒员工。 3.数据传输异常时，原因是否查明并报告HSE管理部。 | 部门不涉及
|  | 5.8.2.10 The production and operation department shall organize the self-inspection on envi-ronmental protection facilities and on-line automatic monitoring instruments at least once a month, and send the self-inspection report to the HSE Dept., the contents of which shall in-clude the operation status of the facilities, the discharge of pollutants, the sampling and moni-toring status and the continuous operation records. 生产运行部门每月至少组织一次对环境保护设施、在线自动监控仪表的自查，并将自查报告发给HSE管理部。内容包括：设施的运行状况、污染物排放情况、取样和监测情况、连续运行记录等。 | 1. Check the self-inspection report to see whether self-inspection of environmental protection facilities and online automatic monitoring instruments is organized every month and a self-inspection report is formed. 2. Whether the content of the self-inspection report meets the system requirements. 3. Whether the self-inspection report is sent to the HSE Management Department. 1.查自查报告，是否每月组织对环保设施、在线自动监控仪表开展自查，并形成自查报告。 2.自查报告内容是否满足制度要求。 3.自查报告是否发给HSE管理部。 | 部门不涉及
|  | 5.8.2.12 Be responsible for the management and operation of on-line automatic monitoring instruments, and submit the self-inspection, checking and mandatory verification reports to the HSE Dept. on time. 质量检验部、仪表控制部负责在线自动监控仪表管理和运行，应按时向HSE管理部提交自查、校核、强检报告。 | Check the self-inspection, calibration and compulsory inspection reports of online automatic monitoring instruments, and whether the quality inspection department and instrument control department submit relevant reports on time. 查在线自动监控仪表自查、校核、强检报告，质量检验部、仪表控制部是否按时提交相关报告。 | 部门不涉及
|  | 5.8.2.13 The HSE Dept. and relevant departments have the right to supervise the operation of the environmental protection facilities, and the production and operation department shall faithfully reflect the operation conditions. HSE管理部及相关部门有权监督环境保护设施运行情况，生产运行部门应如实反映运行情况。 | Check the environmental protection facility operation and management records to see whether they truthfully reflect the operation status of the environmental protection facilities. 查环保设施运行管理台账，是否如实反映环保设施运行情况。 | 是
|  |  | 部门废弃物管理台账中未见空油桶/化学品桶的转移处置记录。 | 本月两次转移空桶，都已登记
|  |  | 部门未建立烟气（烟尘）监测数据统计台帐。 | 每月监测数据台账已更新
| Management on environmental protections in startup and shutdown as well as maintenance and repair 开停工及检维修环保管理 | 5.9.1.2 Detailed environmental protection management measures shall be given in the schemes of device startup and shutdown as well as maintenance and repair. 装置开、停工、检维修方案中应有详细的环保管理措施。 | Check whether measures are taken to prevent materials in the plan 检查开停工方案，检查相关环境保护措施 | 符合要求
|  | 5.9.1.3 The environmental protection devices shall be started up first and shut down later to ensure the effective disposal of pollutants. 环保装置应做到先开后停，确保污染物得到有效地处置。 | Check the site to see whether the environmental protection devices follow the principle of start-first-stop. 查现场，环保装置是否遵循先开后停原则。 | 遵循
|  | 5.9.1.5 During the period of startup and shutdown as well as maintenance and repair, all ab-normal discharge of pollutants shall be conducted in an orderly manner by applying for ap-proval. 在开停工及检维修期间，所有异常排污进行排污申请，有序排放。 | During start-up, shutdown, inspection and maintenance, abnormal pollution discharge is carried out in accordance with the approval requirements, and discharged in an orderly manner according to the prescribed emission volume during the prescribed time period. 在开停工及检维修期间，异常排污是否按照审批要求执行，在规定时段按规定排放量，有序排放。 | 已按要求执行
|  | 5.9.2.4 Equipment that may cause pollution to clean effluent systems shall be provided with a special cleaning field for diverting wastewater from clean water during the maintenance and repair work. 有可能造成清净下水系统污染的设备应设立专门的清洗场，保证检维修期间的清污分流。 | Whether the flushing equipment is in the proper position to prevent the flushing material from entering the rainwater system 冲洗设备是否在合适的位置，防止冲洗物进入雨水系统 | 位置合适
|  | 5.9.2.5 The stacking sites shall be set up for solid wastes which shall be well-marked by classification to properly keep the solid wastes to prevent pollution. 设立固体废物堆放场所，分类做好标识，妥善保管固体废物，防止发生污染。 | The maintenance work is completed, whether the site is completed and the materials are cleaned up, and whether the waste generated is disposed of in compliance with regulations 检修作业完工，现场是否工完料尽场地清，产生的废弃物是否合规处置 | 符合
|  | 5.9.3.4 It is strictly prohibited to discharge sump oil, various residual liquid, etc. into sewage pipelines, open trenches or rainwater drainage systems. 严禁将污油、各类残液等排入污水管线、明沟或雨排系统。 | Check the scene to see if there is any dirty oil or various residual liquids entering the sewage pipes, open ditches or storm drains. 查现场，是否存在污油、各类残液进入污水管线、明沟或雨排。 | 不存在
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (1) The desulfurization device and the sulfur-containing sewage system as well as equipment like the towers and containers that are in contact with the sulfur-containing and ammonia-containing media in the shutdown device shall be deodorized by the use of effective additives before the purging. 对停工装置中的脱硫装置和含硫污水系统及接触含硫、氨介质的塔、容器等设备在吹扫前使用有效助剂进行脱臭处理。 | Check the HSE control plan to see whether the desulfurization device, sulfur-containing wastewater system, and towers, containers and other equipment that come into contact with sulfur-containing and ammonia media are deodorized with effective additives before purging. 查HSE管控方案，脱硫装置和含硫污水系统及接触含硫、氨介质的塔、容器等设备在吹扫前是否使用有效助剂进行脱臭处理。 | 已按要求落实
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (2) The device shall be purged in an airtight manner. 装置吹扫应采取密闭方式。 | Check the purge plan to see if a closed purge plan has been formulated for the device purge. Check the site to see if there is any odor when the device is purged on site. 查吹扫方案，装置吹扫是否制定密闭吹扫方案。 查现场，装置改现场吹扫是否会有异味。 | 无异味
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (4) The flare shall be timely adjusted to eliminate smoke and steam in the shutdown process, so as to ensure safe emission of burnt waste gas to avoid generation of black smoke. 停车过程中，及时调整火炬消烟蒸汽，安全排放燃烧废气，避免冒黑烟。 | Check the scene to see if there is any black smoke coming out of the torch. 查现场，火炬是否存在冒黑烟情况。 | 没有
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (5) When the device undergoes purging of the sour gas system, it is first blown to the flare for burning. After the H2S content of the system is less than 10mg/m3 by sampling analysis, and confirmed on the site by the environmental protection management personnel of the HSE Dept., the device can be emptied on the spot. 装置吹扫酸性气系统时，先吹往火炬燃烧，经采样分析系统H2S含量小于10mg/m3，并经HSE管理部环保管理人员现场确认后，装置才可就地放空。 | 1. Check LIMS to see if the H2S sampling analysis is less than 10mg/m3 before the acid gas purge is vented. 2. Check the site to see if there is any odor when the acid gas purge is vented. 1.查LIMS，酸性气吹扫现场放空前H2S采样分析是否小于10mg/m3。 2.查现场，酸性气吹扫现场放空是否有异味。 | 符合要求
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到 (6) Prior to steam purging of towers, tanks and other containers containing benzenes and hydrocarbons, the system must undergo nitrogen displacement and water flushing. After the total hydrocarbon content of the system is less than 0.5％ by sampling analysis, and con-firmed on the site by the environmental protection personnel of the HSE Dept., the system can be emptied on the spot. 含有苯类、烃类的塔、罐及其他容器蒸汽吹扫前，系统必须进行氮气置换和水冲洗，并经采样分析，系统总烃<0.5％，经HSE管理部环保人员现场确认后，方可就地放空。 | 1. Check LIMS to see if the total hydrocarbon sampling analysis of the system is less than 0.5% before the steam purge of towers, tanks and other containers containing benzene and hydrocarbons is vented on site. 2. Check the site to see if there is any odor when the steam purge of towers, tanks and other containers containing benzene and hydrocarbons is vented on site. 1.查LIMS，含有苯类、烃类的塔、罐及其他容器蒸气吹扫现场放空前系统总烃采样分析是否小于0.5％。 2.查现场，含有苯类、烃类的塔、罐及其他容器蒸气吹扫现场放空是否有异味。 | 符合
|  | 5.9.3.6 Steam purging & cleaning, the following points shall be achieved: 蒸煮、清洗时应做到： (4) Equipment cleaning water is prohibited from discharging into the rainwater drainage sys-tems. 设备清洗水禁止排入雨排系统。 | Check on site to see whether the equipment cleaning water enters the rainwater drain. 查现场，设备清洗水是否进入雨排。 | 没进入
|  | 5.9.3.10 During the period of shutdown, synchronous monitoring shall be carried out on the sewage outlets, waste gas emissions and the ambient atmosphere. 停工期间应对污水排放口情况、废气排放情况和环境大气进行同步监测。 | Check LIMS to see whether the Quality Inspection Department conducts simultaneous monitoring of sewage outlet conditions, waste gas emissions and ambient atmosphere as required. 查LIMS，质检部是否按要求对对污水排放口情况、废气排放情况和环境大气进行同步监测。 | 是
|  | 5.9.4 Maintenance and repair stage 检维修阶段 5.9.4.1 Effective measures shall be taken to prevent the residual materials in the dismantling process of the equipment from falling to the ground. 应采取有效措施，防止设备拆解过程的残余物料落地。 | 1. Check the maintenance plan to see whether the maintenance plan effectively identifies the risk of residual materials during the equipment disassembly process and whether corresponding control measures are formulated. 2. Check the site to see whether there are residual materials on the ground during the equipment disassembly. 1.查检维修方案，检维修方案制定是否有效识别出设备拆解过程存在残余物料的风险，是否制定相应控制措施。 2.查现场，设备拆解是否存在残余物料落地。 | 已制定方案
|  | 5.9.4 Maintenance and repair stage 检维修阶段 5.9.4.2 The equipment that may cause pollution to the clean effluent system shall be sent to the designated place for cleaning to prevent pollution to the rainwater drainage system. 应将有可能造成清净下水系统污染的设备送到指定地点清洗，防止污染雨排系统。 | 1. Check the maintenance plan to see whether the maintenance plan identifies that sewage will pollute the rainwater drainage system during equipment cleaning, and whether the equipment is considered to be sent to a designated location for cleaning. 2. Check the site to see whether effective measures are taken during the cleaning process to prevent pollution of the rainwater drainage system if the equipment cannot be sent to a designated location for cleaning. 1.查检维修方案，检维修方案制定是否辨识设备清洗过程中污水会污染雨排系统，是否考虑将设备送到指定地点清洗。 2.查现场，设备如果无法送到指定地点清洗，清洗过程是否采取有效措施防止污染雨排。 | 移送至指定地点
|  | 5.9.4 Maintenance and repair stage 检维修阶段 5.9.4.3 During maintenance and repair of the device, the rainwater drainage system, wastewater pool and sewage discharge pipe network of the device shall be maintained and repaired simultaneously. 装置检维修时，应同时对装置的雨排系统、废水池和排污管网进行检维修。 | Check the maintenance plan to see whether the drainage system, wastewater tank and sewage pipe network of the device have been inspected and maintained. 查检修计划，是否对对装置的雨排系统、废水池和排污管网进行检维修。 | 已排计划
|  | 5.9.4.4 The process medium wastes (such as polymer, sludge, bottom mud , waste catalysts, etc.) cleaned out of the equipment and pipelines shall be transported to the designated place in time. 设备及管线清理出的工业固体废物（如聚合物、油泥、底泥、废催化剂等）要及时运至指定场所， | 1. Check the HSE control plan to see if the storage location and management requirements of industrial solid waste are clearly stated in the plan. 2. Check the site to see if the industrial solid waste cleared from the equipment and pipelines is transported to the designated location as required. 1.查HSE管控方案，方案中是否明确工业固废的存放地点和管理要求。 2.查现场，设备及管线清理出的的工业固废是否按要求运至指定场所。 | 已移至指定地点
|  | 5.9.4.5 Waste classification management shall be strictly implemented, where hazardous wastes and general wastes shall be collected separately, valuable materials and valueless ma-terials collected separately. 严格执行垃圾分类管理，危险废物与一般废物分开收集，有价物料与无价物料分开收集。 | Check the site to see whether hazardous waste and general industrial solid waste are collected separately. Check whether valuable materials and non-valuable materials are collected separately. 查现场，危险废物、一般工业固废是否分开收集。有价值物料与无价值物料是否分开收集。 | 已做好垃圾分类
|  | 5.9.4.6 The pool cleaning and tanks cleaning shall be carried out under schemes. The envi-ronmental protection measures shall have undergone the environmental protection review, and measures of sludge “reduction” shall be taken. The generated sludge with higher oil con-tent shall be sent to the Power Dept. for treatment, and those with lower oil content and with liquidity shall be sent to the sewage farm of Utilities Dept. 清池、清罐有方案，环保措施经过环保审查，采取油泥“减量化”措施。产生的油泥含油率较高的送往热电部处理，含油率较低且有流动性的送往公用工程部污水处理场。 | 1. Whether an environmental protection plan has been formulated for pool and tank cleaning and has been reviewed by the environmental protection department of the HSE department. 2. Whether an application has been submitted for sludge disposal and whether it has been disposed of in accordance with the approval requirements. 1.清池、清罐是否制定环保方案，并经HSE部环保专业审查。 2.油泥处置是否提交申请，并按审批要求处置。 | 已按要求落实
|  | 5.9.4.7 During the period of shutdown for maintenance, the vegetation shall not be damaged or polluted, nor the soil or surface water shall be polluted. 停工检修期间不得损坏和污染植被，不污染土壤与地表水。 | Check the site to see whether the vegetation has been damaged or contaminated during the maintenance process, and whether the soil and surface water have been polluted. 查现场，检修过程是否存在损坏、污染植被，是否存在污染土壤和地表水的情况。 | 不存在污染
|  | 5.9.4.8 All departments shall be responsible for the environmental protection management of the external construction teams and the maintenance and operation assurance teams within the scope of their own departments. 各部门负责本部门范围内的外来施工队伍、维护保运队伍的环保管理。 | 1. Conduct on-site inspections to check whether the environmental protection management of external construction teams and maintenance and transportation teams is in place. 1.现场检查，外来施工队伍、维护保运队伍的环保管理是否执行到位。 | 已按要求执行
| Management on environmental protection statistics 环保统计管理 | 5.12.2.2 All departments shall undertake the responsibility for the accuracy of the statistical data of their own departments, and report the environmental protection statistics of the pre-ceding month to the HSE Dept. each month. 各部门对本部门统计数据准确性负责，每月上报上月环保统计给HSE管理部。 | Check the environmental statistics ledger to see whether the statistical data is accurate, whether it has been reviewed by the department, and whether it has been submitted to the HSE Management Department on time. 查环保统计台账，统计数据是否准确，是否经本部门审核，并按时提交HSE管理部。 | 已按要求执行
|  | 5.12.3 Management on environmental protection signs 环保标识管理 Refer to the provisions of HSE Signs in Section 5.11 of the HSE Comprehensive Manage-ment System. 参照《HSE综合管理制度》中第5.11部分HSE标识的规定。 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | Check the on-site environmental protection signs to see if any are missing or damaged. 查现场环保标识，是否存在缺失、损坏。 | 无缺失，损坏
| Environmental accident and incident management 环保事故、事件管理 | Refer to the provisions of Accident and incident management in Section 5.17 of the HSE Comprehensive Management System. 参照《HSE综合管理制度》中第5.17部分事故、事件管理的规定。 5.17.5.1 incident and accident management requirements事故、事件报告要求 After an operation department accident or incident occurs, the occurrence department shall immediately report to the dispatch room, the person in charge of the department and the HSE Management Department, and submit a Preliminary Report Form of Accident (Incident) to the HSE Department via email within 24 hours. 发生事件、运行部级事故后，发生部门应立即报告调度室、本部门负责人和HSE管理部，24小时内通过邮箱向HSE管理部提报《事故（事件）初步报告表》。 | Check the "Preliminary Report Form for Accident (Incident)" to see whether the report is submitted within the time limit. 查《事故（事件）初步报告表》，是否按时限要求报告。 | 已按要求落实，本月本部门未发生事故事件。
|  | 5.17.6.1 Incident investigation 事件调查 Where the incident submitted to the "Accident (incident) Preliminary Report Form", the occurrence department shall organize the incident investigation within one week after the occurrence of the incident, prepare the incident investigation record form, and the department shall file the record. 凡提报《事故（事件）初步报告表》的事件，发生部门应在事件发生后一周内组织事件调查，编写《事故（事件）报告表》，报HSE管理部。 | Check the "Accident (Event) Report Form" to see whether an investigation into the environmental incident has been organized and the "Accident (Event) Report Form" has been submitted within the time limit. 查《事故（事件）报告表》，是否按时限要求对环保事件组织调查并提交《事故（事件）报告表》。 | 已按要求执行
|  | 5.17.6.2 Accident investigation 事故调查 （1）In the event of an departmental level accident, each operation department shall organize its own investigation, and the competent department of the company may participate in the investigation. After the investigation is completed, the accident department shall fill in the Accident (Incident) Report Form and submit it to the HSE Department. If the accident involves several departments, the competent department shall organize the investigation, and the competent department shall designate relevant departments to fill in the Accident (Incident) Report Form and submit it to the HSE Department. 发生运行部级事故，由各运行部自行组织调查，公司主管部门可参与调查。调查完成后，事故发生部门填写《事故（事件）报告表》，并提报HSE管理部；事故涉及到几个部门的，由主管部门组织调查，并由主管部门指定相关部门填写《事故（事件）报告表》，并提报HSE管理部。 | Check the "Accident (Incident) Report Form" to see whether an investigation into the environmental accident has been organized and the "Accident (Incident) Report Form" has been submitted within the time limit. 查《事故（事件）报告表》，是否按时限要求对环保事故组织调查并提交《事故（事件）报告表》。 | 已按要求执行
|  | 5.17.6.3 In the course of accident liability investigation, it shall make a thorough investigation of direct cause, indirect cause, primary cause and minor cause of the accident, and define personnel directly responsible for the accident and those mainly responsible for the accident. 在调查事故责任时，要查清事故的直接原因、间接原因，分清事故的直接责任者、主要责任者。 | Check the "Accident (Incident) Report Form" to find out the direct and indirect causes, and distinguish the direct and main responsible persons for the accident. 查《事故（事件）报告表》，是否查清直接原因、间接原因，分清事故的直接责任者、主要责任者。 | 已按要求执行
|  | 5.17.7.2 After the handling of accidents and events, the department shall fill in the Registration Form of Accident (Event) Four and Accident Management Statistics Account, and other relevant departments shall fill in the Implementation Form of Accident Prevention Measures of Relevant Departments according to the requirements of the HSE Management Department, and report to the HSE Management Department for record. 事故、事件处理结束后，部门填写《事故（事件）四不放过登记表》、《事故管理统计台帐》，其他相关部门按HSE管理部的要求填写《相关部门事故防范措施落实表》，并上报HSE管理部备案。 | 1. Check the "Four No-Let-Go Registration Form for Accidents (Events)" and "Accident Management Statistical Ledger". 2. Check the "Accident Prevention Measures Implementation Form of Relevant Departments". 1.查《事故（事件）四不放过登记表》、《事故管理统计台帐》。 2. 查《相关部门事故防范措施落实表》。 | 已按要求执行
|  | 5.17.7.3 In case of cover-up, false reporting and deliberate delay in reporting of an accident, intentional destruction of accident site, concealing of accident truth, objection to receive investigation or provide any information and data without justified reasons, punishment shall be aggregated. 事故发生后隐瞒不报、谎报、故意拖延不报、故意破坏事故现场、隐瞒事故真相，或者无正当理由，拒绝接受调查以及拒绝提供有关情况和资料的，加重处理。 | 1. Ask on-site employees whether there are any environmental accidents (incidents) that are concealed, falsely reported, or deliberately delayed. 2. Check the accident site to see if the accident site has been deliberately damaged. 3. Investigate and collect evidence and interview personnel about environmental accidents (incidents) to see if there are any who refuse to accept the investigation and refuse to provide relevant information and materials. 1.询问现场员工，是否存在环保事故（事件）隐瞒不报、谎报、故意拖延不报。 2.查事故现场，是否存在事故现场被故意破坏情况。 3.环保事故（事件）调查取证及人员访谈，是否存在拒绝接受调查以及拒绝提供有关情况和资料的。 | 无瞒报
| Environmental protection training 环保培训 | Refer to the provisions of HSE education, training and competency building in Section 5.10 of the HSE Comprehensive Management System. 参照《HSE综合管理制度》中第5.10部分HSE教育、培训和能力建设的规定。 5.10.3.1 New employees in operation positions shall receive 3 level HSE training, the time is 72 academic hours, and the annual refresher training time is not less than 20 academic hours, and they can only take the post after passing the examination. 生产操作岗位新员工应接受三级HSE培训，时间为72学时，每年再培训时间不少于20学时，并经考试合格后方可上岗。 | Check whether the HSE training materials and annual retraining contents of the operation department and team level cover environmental protection content. 查运行部、班组级HSE培训材料和年度再培训内容，是否涵盖环保内容。 | 涵盖环保内容
|  | 5.10.4 Special HSE training HSE专项培训 HSE special training shall be implemented temporarily according to the training plan formulated by the HSE Management Department and the Operation Department or according to the current safety situation according to the needs of employees and the different characteristics of each position, including but not limited to safety, environmental protection, occupational health, fire protection, accident cases, emergency plans, laws and regulations, HSE operating procedures, etc. HSE专项培训应根据员工需求和各岗位不同特点按照HSE管理部及运行部制定的培训计划或根据当前安全形势临时实施，包括但不限于安全、环保、职业健康、消防、事故案例、应急预案、法律法规、HSE操作规程等。 | Check the department's annual HSE training plan and records to see whether an environmental protection training plan has been developed and completed. 查部门年度HSE培训计划和记录，是否制定并完成环保培训计划。 | 已制定
|  | 5.10.6.1 Before contractor personnel enter the factory, the HSE Management Department will conduct Level I HSE training. Before entering the operation area of each unit, the Operation Department will conduct Level II HSE training. After the training, the contractors must pass the examination and conduct safety briefings before operation. Each operating department should keep training records. 承包商人员入厂前由HSE管理部实施一级HSE培训，进入各装置区域作业前由运行部实施二级HSE培训，培训结束经考试合格，作业前进行安全交底后方可作业。各运行部门应做好培训记录。 | Check the contractor's Level 2 HSE training materials to see if they include environmental protection content and requirements. 查承包商人员二级HSE培训材料，是否包含环保内容和要求。 | 已包含
| Assessment on environmental protection 环保考核 | Refer to the provisions of HSE Assessment in Section 5.15 of the HSE Comprehensive Man-agement System. 参照《HSE综合管理制度》中第5.15部分HSE考核的规定。 5.15.2 Each department shall refer to the Company's "Performance Appraisal Measures" or refine the performance appraisal system of its own department to assess, reward and punish the HSE work of its own department, and establish the HSE assessment reward and punishment ledger. 各部门引用公司《绩效考核办法》或细化为本部门绩效考核制度，对本部门的HSE工作情况进行考核奖惩，并建立HSE考核奖惩台帐。 | Check the HSE assessment reward and punishment ledger to see whether the content of the ledger involves environmental protection professional rewards and punishments. 查HSE考核奖惩台帐，台账内容是否涉及环保专业奖惩。 | 涉及
| Environmental protection management during operation 作业过程环境保护管理 | 5.18.2 After the work is completed, each construction unit must ensure that the site is "clean", that is: there is no relics, no oil pollution, and no damage on the construction site; the site is cleared after the work is completed and the local department inspects it. 作业结束后，各施工作业单位必须做到现场“三无一清”，即：施工现场无遗物、无油污、无损害；工完料尽场地清，由属地部门监督落实。 | Check the implementation of “three no’s and one clear” at the work site. 查作业现场“三无一清”执行情况。 | 现场按规定落实
|  |  | 芳烃装置D550A装卸剂作业HSE管控方案未对粉尘开展环境因素识别并制定措施。同类问题在岐化反应器换剂HSE管控方案中也存在。 | 本月一项技改，在管控方案里涉及环保内容。
|  | 5.18.3 Each unit should formulate an emergency operation plan for the installation operation process, and take emergency preventive measures to reduce the impact and impact on pollu-tion control facilities and sewage treatment systems, ensure treatment effects, and prevent the occurrence of environmental pollution accidents and incidents. 各单位在制定HSE管控方案时，应识别环境风险，制定环境保护措施，预防环境污染事故、事件的发生。 | 1. Check the HSE control plan for the operation to see whether environmental risks are identified and environmental protection measures are formulated. 2. Check the operation site to see whether the environmental protection requirements in the HSE control plan are effectively implemented. 1.查作业HSE管控方案，是否识别环境风险并制定环保措施。 2.查作业现场，HSE管控方案中的环保要求是否得到有效落实。 | 本月一项技改，在管控方案里涉及环保内容。
| 5.1 Management principles and content 管理原则和内容 | 5.1.1 The principle of "whoever is in charge is responsible" for gas control and safety work shall be adhered to, and a responsibility system for gas control and safety shall be implemented. Every employee has the obligation to maintain fire prevention safety, protect fire prevention facilities, prevent fires, report fire alarms, provide fire protection and participate in emergency rescue. 消气防安全工作坚持“谁主管、谁负责”的原则，实行消气防安全责任制。每位员工都有维护消气防安全、保护消气防设施、预防火灾、报告火警、气防救护和参加应急救援的义务。 | Whether the fire safety responsibility system has been implemented and the responsible persons for fire protection at the post have been clearly identified; 是否落实防火安全责任制，并明确岗位消防责任人； | 防火台账已记录
|  |  | 1、Whether fire safety knowledge training is organized for each post so that personnel can master firefighting skills; 是否组织各岗位学习进行消防安全知识培训，使人员掌握消防技能； 2、Whether the department leaders participated and whether the relevant records were signed by the leaders 部门领导是否参与，相关记录有无领导签名 | 本月消防技能竞赛人员考试完成，成绩归档。
| 5.3.11 Purchase requisition of fire-fighting equipment, facilities and appliances 消气防设备 设施器材申购 | 5.3.11.5 Each professional department shall regularly purchase fire fighting equipment, facilities and spare components in advance according to the need of the site conditions and to meet the need of the situation. The purchase requisition of fire fighting equipment, facilities and appliances shall be performed as per the company’s relevant regulations. 各专业管理部门根据现场需要，定期提前提报消防设备、器材以及备品备件，以满足现场的需要，消防设备设施器材的申购工作按公司有关规定执行。 | According to the needs of the site, whether fire-fighting equipment, instruments and spare parts are purchased regularly in advance to meet the needs of the site; 根据现场需要，是否定期提前采购消防设备、器材以及备品备件，以满足现场的需要； | 已报采购计划
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.11.2 When the production equipment is stopped for maintenance, the fire-fighting water system shall not be stopped. If the system needs to be stopped, it shall be restored before the equipment is stopped for maintenance. If it’s really necessary to stop the use of fire water when the equipment id stopped for maintenance, it shall be approved by the leader in charge of the company. 生产装置停产检修时，消防水系统不得停用；若需停用，应在装置停产检修前予以恢复；装置停产检修期间，确需停用消防水，应由公司主管领导批准。 | When the production equipment is shut down for maintenance, is the fire water system shut down? 生产装置停产检修时，消防水系统是否停用； | 不停用
| 5.4 Fire-fighting publicity and training 消防宣传和培训 | 5.4.2 Fire-fighting training for personnel, such as new recruits, transferees and re-appointed staff, shall be performed during the three-level safety education activity by the responsible person of three-level safety education. 新员工、转岗、复岗等人员的消防内容培训，由三级安全教育负责人在进行三级安全教育时予以落实。 | Whether the fire protection content training for new employees, transfer personnel, returning personnel, etc. is implemented during the third-level safety education, and whether records are kept and archived; 新员工、转岗、复岗等人员的消防内容培训，是否在进行三级安全教育时予以落实，并留有记录，存档管理； | 已按要求记录并存档
| 5.4 Fire-fighting publicity and training 消防宣传和培训 | 5.4.3 Each department shall perform fire safety education at least once per quarter. The content shall mainly include: fire-fighting laws and regulations, fire safety institutions and operation rules, fire hazardousness and fire safety measures of the department, operation of fire fighting facilities, knowledge and skills concerning fire alarm, warning, separation, fire extinguishment and rescue, self-rescue and self-escape. 各部门每季度不少于1次消防安全教育；培训内容主要包括：消防法律法规；消防安全制度和操作规程；本部门的火灾危险性和防火措施；消防设施使用和操作；报警、警戒、隔离、灭火以及救人、自救与逃生的知识和技能。 | Whether fire safety education is implemented as required, whether the training content is sound, and whether records are kept and archived; 消防安全教育是否按要求落实，培训内容是否健全，并留有记录，存档管理； | 本月消防技能选拔成绩已记录存档
检查现场空呼，气防柜状态良好，东西齐全。
手机、上岗证齐全
| 5.4 Fire-fighting publicity and training 消防宣传和培训 | 5.4.4 Operators of fire fighting facilities and appliances shall receive special training in operation skills, learn and master corresponding operation skills, and may take the post after passing the examination. 消防设备设施操作人员应经过专门的操作技能培训，学习掌握相应的操作技能，经考试合格后上岗。 | Whether firefighting skills training is carried out to learn and master the corresponding operating skills, and whether they can take up their posts after passing the examination, and whether records are kept and archived; 是否开展消防技能培训，学习掌握相应的操作技能，经考试合格后上岗，并留有记录，存档管理； | 本月已完成消防演练并记录
| 5.5 Fire prevention inspections and hidden danger management 消气防监督检查和隐患治 理 | 5.5.1.1 Fire inspections shall be divided into the company-level and the department-level inspections. At company level, there are monthly fire inspections, special inspections and professional inspections, while at department level, fire inspections are daily inspections. 防火检查分为公司级和部门级；公司级防火检查分为每月防火检查、专项检查和专业检查；部门级防火检查为日检。 5.5.1.2 Contents of fire inspections shall include situations of key fire-control places, integrity of fire fighting equipment, facilities, systems and appliances, shift taking of fire control room, escape routes, safety exits, fire lanes and other unimpeded conditions, integrity of archives and accounts, ratification of fire hazard. 防火检查的内容包括消防重点部位情况；消防设备设施系统及器材的完好性；消防控制室值班情况；疏散通道、安全出口、消防车通道等畅通情况；档案和台账完整情况；火灾隐患整改情况等。 | Whether department-level fire prevention inspections are strictly implemented, and records are kept and archived; 是否严格落实部门级防火检查，并留有记录，存档管理； | 防火检查记录表已按要求记录
| 5.6 Fire-fighting drills, fire-fighting and rescue 消气防演练与灭火救灾 | 5.6.1.1 Each operation department shall formulate special emergency plans and on-site response scheme according to specific situations, and organize regular drills as per the company’s relevant regulations. 各运行部应根据具体情况制定专项应急预案和现场处置方案；各运行部按照公司相关规定定期组织演练。 | Whether on-site emergency drills are conducted regularly; 是否定期开展现场应急演练； | 按年度演练计划每月一次
| 5.6 Fire-fighting drills, fire-fighting and rescue 消气防演练与灭火救灾 | 5.6.1.2 Schemes shall be made before the drills. The scheme shall include scene of the drill, emergency response, gas protection and first aid, evacuation and processing. Fire brigades, gas protection departments and security departments shall also be invited to cooperate in the drill to make it more practical. 演练前，应编制演练方案，方案包括演练情景、应急响应、火灾扑救、气防急救、人员疏散、工艺处理等内容，也可邀请消防、气防、安保配合演练，以使演练更加贴合实际。 | Whether a drill plan has been prepared; whether the content of the plan is complete; 是否编制演练方案；方案内容是否齐全； | 年度演练方案齐全
| 5.6 Fire-fighting drills, fire-fighting and rescue 消气防演练与灭火救灾 | 5.6.1.3 After the drill, it shall be summarized and the emergency response plan of the accident shall be revised according to the drills. 演练结束后应进行总结，根据演练情况对事故应急方案进行修订。 | Whether a summary is conducted after the drill and a summary report is kept; 演练结束后是否进行总结，并留有总结报告； | 本月演练总结已收集
| 5.7 Construction of emergency rescue teams 应急救援队伍建设 | 5.7.2.2 Number of the volunteer fire brigade shall not be less than 60% of the total personnel of the department, and external operators shall be the member of it. In case of personnel changes, each department shall report the change to the HSE Dept. within 30 days. 志愿消防队的人数不少于本部门职工总数的60%，外操人员应为志愿消防队员；若有人员变动，各部门应在30天内将变动情况上报HSE管理部。 | Whether a volunteer fire brigade has been established and whether the number of volunteer fire brigades meets the requirements; 是否建立志愿消防队,志愿消防队的人数是否满足要求； Whether changes in department personnel have been reported to the HSE Management Department within 30 days;" 部门人员发生变动后是否在30天内将变动情况上报HSE管理部； | 上岗员工基本全部为支援消防人员
| 5.8 Fire-fighting records and archives 消防记录和档案 | 5.8.1 Each department shall be responsible for establishing a department-level fire-fighting archive and submit it to the HSE Dept. which shall establish a company-level fire-fighting archive. 各部门负责建立本部门消防档案，并上报HSE管理部，HSE管理部建立公司消防档案。 | Whether departmental fire protection files are established; 是否建立部门消防档案； | 已建立档案，每月末更新。
|  |  | 炼油三部演练记录未及时增添到消防档案中，炼油四部火灾情况和演练记录未及时增添到消防档案中，档案管理需要进一步完善 | 配合消防队开展的演练都记录到消防档案中。
| 5.8 Fire-fighting records and archives 消防记录和档案 | 5.8.2 Content of fire fighting archives shall include basic information on fire safety , fire safety management and other documentations. 消防档案内容包括消防安全基本情况、消防安全管理情况等文件材料。 | Whether the contents of the fire protection files are complete; 消防档案内容是否完备； | 内容建全
[5 empty] | HSE活动记录本：加裂二班赵广旭未补学，加氢四班还未记录 11月30日前整改 | 不考核 |  | 加裂二班 加氢四班

## 日检表 (26)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期：11 MM 19 DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 雨棚除锈刷漆,气分技改线保温
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 盲板隔离
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 今天提问罗庆通，侯雪峰回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  |  | 1040-C102二层三层XM11541 XM11542褪色严重。1040-C102, Levels 2 & 3: extinguisher tags XM11541 and XM11542 are severely faded. |  | 不考核 | 11月27日前整改 | 加裂一班 |  | 毛奕清
|  |  |  | 1030-E202AB东灭火器箱XM11734褪色严重，检查卡签名完全看不清。At 1030-E202AB (east), the fire extinguisher cabinet XM11734 is severely faded, and the inspection card signatures are not readable. |  | 扣1分 |  | 加氢一班 |  | 毛奕清
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态

## 日检表 (25)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期：11 MM 19 DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分保温作业，A203预制焊接挡雨棚
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 气分保温作业，监护人未携带监护人证件, |  | 扣2分 |  | 加裂二班 | 慕斯 | Wafi
|  |  |  | 11月23日二级火票未将第二联给作业，,23日17：08已闭票。 |  | 扣2分 |  | 加裂四班 | munir izz | 毛奕清
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 盲板隔离
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 今天提问罗庆通，侯雪峰回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  |  | 靠近1040-SR101 , XM11745 号灭火器底座锈蚀；请除锈并刷漆恢复，或更换整套灭火器与。 |  | 扣1分 |  | 加裂四班 |  | Wafi
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
[5 empty] | 马国淮，尤小波白副班考试卷鹤低于80，卡柚木低于70分 | 各扣2分 |  | 加裂二班加裂三班加裂四班加氢三班 |  | 江志宁

## 日检表 (24)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期：11 MM 19 DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 加氢界区拆脚手架, 气分技改线保温, 加裂A203雨棚预制
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
|  |  |  | 11月22日 高处票作业人联未交给作业人 |  | 扣2分 |  | 加裂一班 | 翟小杰 | 毛奕清
|  |  |  | 11月23日高处票作业人联未交给作业人。票证关闭时间未填写。 |  | 扣4分 |  | 加裂四班 | munir izz | 毛奕清
|  |  |  | 11月23日 高处票作业人联未交给作业人 |  | 扣2分 |  | 加裂四班 | 白鹤 | 毛奕清
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 盲板隔离
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽考全晓琪回答良好。抽考莱菲，卡尤姆未答对 |  | 各扣2分 |  | 加氢三班 |  | 毛奕清
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态

## 日检表 (21)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期：11 MM 19 DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分装置内动火, 界区外穿管和动火.动火前地沟未覆盖，警戒区域设置不合理。
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 1,11月20日柴油C201脚手架二级火票，高票未给作业人;2,11月19日气分技改线管线焊接一级火票未给作业人 |  | 各扣2分 |  | 加氢三班加裂四班 | 马斯鲁妮娜 | 毛奕清
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 盲板隔离
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽考侯雪峰，罗庆通未答出 |  | 扣2分 | 下个白板再次抽考 | 加氢二班 加裂二班 | 侯雪峰 罗庆通 | 毛奕清
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
|  |  |  | 1020-D103顶XM11751编号褪色 |  | 不考核 | 2025-11-22 | 加氢二班 |  | 毛奕清
|  |  |  | 1040-E102C西XM11199内部积水，请打孔。 |  | 不考核 | 2025-11-22 | 加裂二班 |  | 毛奕清
|  |  |  | 1040-E102C西推车XM11268卡片进水，请增加防护，避免被公司考核 |  | 不考核 | 2025-11-22 | 加裂二班 |  | 毛奕清
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态

## 周检表 (20)
HSE Weekly Checklist for No.2 Refining Department 炼油二部HSE周检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
| Safety Management System 安全管理制度 5.3 HSE hidden danger identification HSE 隐患排查 | 5.3.3.6 All departments shall prepare hidden danger identification form based on their discipline characteristics and actual production conditions and continue to improve such form in practice. 各部门应根据专业特点和实际生产情况制定隐患排查表，并在实际应用中不断持续改进。 5.3.4.1 Control requirements 治理要求 （1）For general hidden danger, departments involved shall immediately organize rectification. 对于一般隐患，由属地所在部门立即组织整改。 （2）For any general hidden danger which can’t be rectified immediately, the department involved shall develop a risk precaution plan and rectification plan, and rectify such danger within a specified timeframe. 对于暂不能整改的一般隐患，由属地部门制定风险防范措施和整改计划，限期整改。 5.3.6.1 All departments shall establish Hidden Danger Identification & Control Account. 各部门应建立《隐患排查治理台账》。 5.3.6.2 The hidden danger treatment should be recorded according to the "HSE Hidden Danger Investigation and Management Ledger" to achieve closed-loop rectification. 隐患治理情况应按《HSE 隐患排查治理台账》进行记录，做到闭环整改。 | Does the hidden danger investigation table meet the investigation requirements 隐患排查表是否满足排查要求 | 加氢12月隐患5个，加裂12月隐患20个
|  |  | Whether the hidden danger investigation and management record is updated in time 隐患排查治理台账是否及时更新 | 已更新至最新版本
|  |  | Whether all staff are trained on hidden danger management 是否组织全员培训隐患治理情况 | 列入每月副班培训中
|  |  | Is the rectification carried out as planned 是否按计划整改 | 有条件的将立即整改
气分技改线动火，加氢C201脚手架拆除
手机及上岗证已按要求上墙
| Safety Management System 安全管理制度 5.4 Management of hazardous chemicals 危险化学品管理 | 5.4.2.2 The HSE management department shall supervise the establishment of hazardous chemicals ledger by all departments.. HSE 管理部监督各部门建立危险化学品台帐。 5.4.2.4 Each operation department must carry out targeted training on the knowledge of hazardous chemicals according to the hazardous chemicals involved in its own department,and staff shall be familiar with information on safety technology of hazardous chemical involved in the post to ensure stable operation and personal safety in production, storage, use, transportation and disposal of hazardous chemicals. 各运行部必须根据本部门涉及的危险化学品开展针对性的危险化学品知识培训，建立本部门《化学品普查表》与《危险化学品台帐》。员工应熟悉本岗位涉及的危化品安全技术信息，以保证危险化学品生产、储存、使用、运输、废弃处置等环节的平稳操作和人身安全。 5.4.2.5 Before using hazardous chemicals, the staff must know and grasp relevant MSDS andsafe operation instructions of hazardous chemicals, take relevant precautionary measures and prevent personal injuries. 员工使用危险化学品时，必须了解和掌握相应危险化学品安全技术说明书和安全操作规程有关内容，并采取相应的防范措施，避免发生人身伤害事故。 | Does the department have a hazardous chemicals register 部门是否建立危险化学品台账 | 已更新至最新版本（二部危化品台账）
|  |  | Whether to organize full-staff learning 是否组织全员学习 | 已放在外操室电脑供学习
| Safety Management System 安全管理制度 5.14.Hydrogen sulfide prevention 防硫化氢中毒安全管理 | 5.14.1 All departments shall set up eye-catching warning signs in both Chinese and English in places where hydrogen sulfide leakage may occur, and hydrogen sulfide warning signs shall be set up in eye-catching places in workplaces where hydrogen sulfide exists. A wind vane shall be set in the eye-catching position of the unit. 各部门在可能发生硫化氢泄漏的场所设置醒目的中英文警示标识，存在硫化氢的工作场所应在醒目位置设置硫化氢告知牌。装置醒目位置应设置风向标。 5.14.2 All personnel having access to hydrogen sulfide hazard area shall carry portablehydrogen sulfide alarms and protection devices as required. 所有进入可能存在硫化氢等有毒有害气体区域的巡检或作业的人员，必须佩戴相应的便携式气体检测仪和防护器具。集中作业时，作业小组应至少佩戴 1 台便携式气体检测仪。 5.14.3 The site concentration should be monitored at any time when the acid water, gas escape site, drain port, sampling port, storage tank metering port and other hidden parts are active. 在酸性水、瓦斯逸出部位、排液口、采样口、储罐计量口等隐患部位活动时，应随时监控现场浓度。 5.14.4 When entering hydrogen sulfide hazard area for patrol, operators shall conduct individual protection well and carry portable hydrogen sulfide alarm. In case of operation in hydrogen sulfide hazard area, it shall wear isolated respirator, set up warning signs around operation points and assign special personnel for monitoring. 员工在涉及接触硫化氢等有毒有害气体作业时，应做好个体防护，佩戴便携式气体检测仪和适宜呼吸防护用品，并有专人进行监护。 5.14.5 According to the working environment of different posts, all departments shall equip the operators with appropriate protective equipment. When the concentration of hydrogen sulfide is less than 50mg/m3, filter type anti-gas appliances can be used; When the hydrogen sulfide concentration is greater than 50mg/m3 or in the area where the medium leakage occurs and the concentration is unknown, isolated respiratory protective equipment should be used,and the gas supply device of the protective equipment should be placed on the upwind side. 各部门根据不同岗位的工作环境为作业人员配备适量适用的防护器材。当硫化氢浓度低于50mg/m3 时，可以使用过滤式防毒用具；当硫化氢浓度大于 50mg/m3 或在发生介质泄漏、浓度不明的区域内应使用隔离式呼吸防护用具，防护用具的供气装置应置于上风侧。 5.14.6 It is forbidden for any person to enter the area where hydrogen sulfide poisoning may occur without proper protective equipment, and it is forbidden to take off the protective equipment in the toxic area. 禁止任何人员不佩戴合适的防护器具进入可能发生硫化氢中毒的区域，禁止在有毒区内脱卸防毒用具。 5.14.7 When the hydrogen sulfide detection instrument alarms, the panel operator should remind the site personnel in time, the operator should wear protective equipment, check the leak point, prepare protective equipment and report to the superior, and evacuate the downwind personnel, prohibit all fire operations, quickly identify the cause of the leak and control the leak. 硫化氢检测仪器报警时，内操应及时提醒现场人员，作业人员应佩戴防护用具、检查泄漏点、准备防护用具并向上级报告，同时疏散下风向人员，禁止一切动火作业，迅速查明泄漏原因并控制泄漏。 5.14.8 Operation in hazardous places that may contain hydrogen sulfide, such as sewage wells and closed containers, shall be carried out in strict accordance with the management requirements of restricted Spaces of this system. 进入污水井、密闭容器等可能含硫化氢的危险场所作业，要严格按照本制度受限空间的管理要求执行。 5.14.9 When construction and maintenance personnel of contractors enter hydrogen sulfide hazard area to work, operation departments where they belong to shall organize construction contractors to conduct risk identification and notification of hydrogen sulfide hazards in operation area, and provide necessary protective devices and emergency rescue facilities. 承包商作业人员在涉及硫化氢等有毒有害气体环境中作业时，属地部门应对承包商作业人员进行硫化氢等有毒有害气体防中毒防窒息安全培训和安全交底，为其提供必要的呼吸防护器具和应急救护设施如正压式呼吸器，长管呼吸器等。 5.14.10 Any operator which is likely to come in contact with poisonous and harmful gases such as the hydrogen sulfide shall take trainings on poisoning and suffocation prevention and shall only take the job after being tested to be qualified. 凡可能接触硫化氢等有毒有害气体的操作人员，应接受防中毒、防窒息安全教育，经考核合格，方可上岗操作。 5.14.11 Departments that may have hydrogen sulfide leakage shall formulate emergency rescue plans and establish a first aid network, ensure that on-site first aid, evacuation and escort, and transport rescue channels are unblocked, conduct regular drills on emergency plans, and revise and improve them in time. 可能存在硫化氢泄漏的部门要制定应急救援预案并建立急救网络，保证现场急救、撤离护送、转运抢救通道畅通，对应急预案定期进行演练，并及时进行修订完善。 | Have employees been trained to prevent hydrogen sulfide poisoning 是否对员工进行防硫化氢中毒培训 | 已全员考试验收
Comprehensive Management 综合管理 | 5.2 HSE organization HSE 组织机构 | 5.2.2 Each department shall establish a safety management organization and establish the corresponding HSE Organization Ledger 各部门应建立安全管理组织机构，并建立相应的《HSE组织台帐》 | Whether the Organizational Ledger has been established and updated in a timely manner 是否建立了组织机构台帐，是否及时进行了更新 | 组织机构台账已建立，更新及时.
| 5.3 HSE policies and objectives HSE方针 | People-oriented, compliance with laws and regulations, community harmony, environmentfriendly, risk controllable. 以人为本、依法合规、社区和谐、环境友好、风险可控。 | Are employees clear about the company's policies, goals and commitments? 员工是否清楚公司方针目标与承诺 | 提问员工回答良好
| 5.4 HSE commitment HSE承诺 | 5.4.1 Abide by Brunei's laws and regulations, respect local customs and habits, and maintain a consistent attitude towards HSE in all business areas. 遵守文莱法律、法规，尊重当地风俗习惯，在所有业务领域对HSE的态度始终如一。 5.4.2 Care for life and health, protect the ecological environment, always adhere to zero tolerance for violations, and pursue the goal of zero injury, zero pollution, and zero accidents. 关爱生命健康，保护生态环境，始终坚持违章零容忍，追求零伤害、零污染、零事故的目标。 5.4.3 In order to ensure the achieve the goal, provide human, material and financial resources to support. 为保证目标的实现，提供人力、物力和财力等资源支持。 5.4.4 Regularly report HSE performance to the Brunei government, account for the needs of stakeholders such as investors, customers, and contractors, and actively accept supervision from all parties around us to achieve continuous improvement. 定期向文莱政府公布HSE业绩，关注投资者、客户、承包商等利益相关方需求，主动接受社会各界监督，实现持续改进。 | Are employees clear about the company's policies, goals and commitments? 员工是否清楚公司方针目标与承诺 | 提问员工回答良好
| 5.9 HSE meeting HSE 会议 | 5.9.2.3 Each department holds a regular HSE meeting once a week. 各部门 HSE 例会每周召开一次。 5.9.3.3 HSE regular meeting of each department 各部门 HSE 例会 （1） Communicate the requirements of HSE meetings at all levels of the company and the recent safety production situation of the company. 传达公司各级 HSE 例会的要求及近期公司安全生产形势。 （2） Arrange HSE work of the department, and solve HSE related problems in the work of each team and staff. 布置本部门 HSE 工作，解决各班组及员工工作中 HSE 相关问题。 | The content of the company's HSE regular meeting was carefully communicated. The HSE regular meeting of this department was held on time. 公司HSE例会内容认真传达 本部门HSE例会按时召开 | 公司例会内容交接班时进行宣贯，并将例会纪要发到群里；部门例会每月末按时召开
| 5.14 HSE assessment HSE考核 | 5.14.2 Each department shall refer to the Company's "Performance Appraisal Measures" or refine the performance appraisal system of its own department to assess, reward and punish the HSE work of its own department, and establish the HSE assessment reward and punishment ledger. 各部门引用公司《绩效考核办法》或细化为本部门绩效考核制度，对本部门的HSE工作情况进行考核奖惩，并建立 HSE 考核奖惩台帐。 | Department’s HSE assessment status 部门的HSE考核情况 | 已在日周月检表内体现
Comprehensive Management 综合管理 | 5.16 Accident and incident management 事故事件管理 | 5.16.4.1 Each operation department shall encourage its employees to report near-miss accidents, and organize investigations and analyses on the near-miss accidents to find out the root cause and prevent the reoccurrence of the accidents. 各运行部门应鼓励并奖励员工报告未遂事件，并组织对未遂事件进行调查、分析，找出事故根 源，预防事故发生。 | Did the department make any request on reporting nearmiss incident? 部门是否对未遂事件进行过要求 | 本周没有未遂事件
|  | 5.16.5.1 incident and accident management requirements 事故、 事件报告要求 After an operation department accident or incident occurs, the occurrence department shall immediately report to the dispatch room, the person in charge of the department and the HSE Management Department, and submit a Preliminary Report Form of Accident (Incident) to the HSE Department via email within 24 hours. 发生事件、运行部级事故后，发生部门应立即报告调度室、本部门负责人和 HSE 管理部， 24 小时内通过邮箱向 HSE 管理部提报《事故（事件） 初步报告表》。 | Whether departmental accidents have been reported as required 部门事故事件是否按要求进行了报告 | 本周无事故事件发生
|  | 5.16.6.1 Incident investigation 事件调查 Where the incident submitted to the "Accident (incident) Preliminary Report Form", the occurrence department shall organize the incident investigation within one week after the occurrence of the incident, prepare the incident investigation record form, and the department shall file the record. 凡提报《事故（事件）初步报告表》的事件，发生部门应在事件发生后一周内组织事件调查，编写《事故（事件） 报告表》 ， 报 HSE 管理部。 | Whether the department's accident incidents are investigated as required 部门事故事件是否按要求开展调查 | 本周无事故事件发生
|  |  | 事故事件台帐已经建立，台帐内容填写不全，维护不及时。 | 事故事件台账已完善
|  | 5.16.7.1 In the course of handling of accidents and incidents, the principles of “Four do not let go”, namely, not allowing any existence of unclear accident causes, not allowing any missing of punishment on accountable parties of the accident, not allowing any failure in implementing the rectification measures and not allowing any failure in mass education targeting relevant liable personnel. 事故、事件处理都要坚持“四不放过”原则，即事故原因未查清不放过、责任人员未处理不放过、整改措施未落实不放过、有关人员未受到教育不放过。 | For accidents in the department, has the department adhered to the "Four Do No-Let-Go" principle? For accidents in other departments of the company, has the department organized employees to learn? 对于部门的事故，部门是否坚持了四不放过原则，对于公司其他部门的事故，是否组织了本部门员工进行学习 | 本周无事故事件发生
|  | 5.5.2.3 Issuance of protection supplies 防护用品发放 （1）The operation department must, according to the requirements of work safety and prevention of occupational hazards, issue to employees PPE with different protection functions and record the issuance of PPE according to “One Person One Record” (See HYBN-T7-08-4001-2024-3 Template of PPE Issuing Records); 运行部门必须根据安全生产和防止职业性危害的需要，发给员工具有不同防护功能的劳动防护用品并按照“一人一卡” 做好劳动防护用品发放记录（参照HYBN-T7-08-4001-2024-3劳动防护用品发放记录模板）; | Whether to establish an employee PPE distribution ledger, whether the ledger is true and complete. 是否建立员工PPE发放台账，台账是否真实、完整。 | 台账已按要求建立，检查没问题
|  |  | XXX部有劳保发放记录但未建立“一人一卡。要求部门按照“一人一卡”劳保发放记录落实。 | 按照一人一卡落实
|  | 5.6.3.1 Operation protection 作业防护 （1）Prior to operation, workplaces where toxic gases may be present shall be tested for toxic gas concentration; 作业前对可能存在有毒气体的工作场所进行有毒气体浓度检测； | Do employees know which toxic and hazardous gases are present in their department and the required protective equipment? 员工是否知道部门有哪一些有毒有害气体？是否懂需要用什么劳动防护用品？ Does management have a list of hazardous substances/MSDS list? Has it been shared to employees? Do employee know how to read/obtain information from a MSDS? 管理人员是否建立部门内部的有毒有害气体清单并做好内部宣贯？员工是否了解MSDS内容？ Does employee know what does IDLH means? 员工是否知道IDLH指什么？IDLH是英文Immediately Dangerous to Life or Health concentration的缩写，指的是直接致害浓度。 | 提问员工回答良好
|  | 5.6.1.4 Employees who participate in poisonous and harmful operations must undergo occupational health education beforehand, keep records of Occupational Health training records (See HYBN-T7-08-4003-2024-1 Occupational Health Training Records) and be provided with effective PPE. 对参加有毒有害作业员工，必须事先进行职业健康教育，做好职业健康培训记录(见HYBN-T7-08-4003-2024-1职业健康培训档案) 并提供有效的劳动防护用品。 5.6.1.7 Occupational Health regular training materials should be recorded and accompanied with proper records (See HYBN-T7-08-4003-2024-1 Occupational Health Training Archives) and filed for storage. 职业健康专业定期学习材料应做好职业健康培训记录 (见HYBN-T7-08-4003-2024-1职业健康培训档案) 并做好存档。 | Check if training records have been established? 培训档案是否按照要求建立？ Check whether OH poster had been published and shared with employees on a timely basis and if records had been logged. 检查职业健康海报是否已及时发布并与员工分享，并查看是否有记录登记 | 本月健康简报已打印放置于外操室外墙上
|  | 5.6.2.1 Noise protection 噪声防护 （1）Employees must wear earplugs or earmuffs when they are exposed to workplaces with excessive noise (greater than 85 dB). 员工接触噪声超标 (大于85dB) 的作业场所，必须配戴防噪声耳塞或耳罩； | Are employees aware of noise exposure limits? 员工是否知道噪声超标指标？ If noise exposure exceeds limit, what should you do? 如果超标，是否知道要佩戴什么防护用品？ | 提问员工回答良好
|  | 5.6.2.2 Noise monitoring 噪声监测 （1）Conduct monitoring of noise at workplaces and noise exposure of employees semiannually; 每半年对作业场所噪声及员工噪声暴露情况至少进行一次监测； | Do employees know the internal noise monitoring points within their department? 员工是否知道部门内部噪声监测点在哪里？ | 提问员工回答良好
|  | 5.6.2.4 Hearing protection 听力保护 （1）According to local laws and regulations, employees at workplaces where there is excessive noise level of more than 85 db(A) should undergo annual audiometry testing to ascertain the impact of excessive noise exposure and to prevent long term hearing loss. 在噪音水平超过85dB(A)的工作场所工作的员工应接受年度听力测试，以确定过度噪音暴露的影响并防止长期听力损失。 | Are employees aware of the health effects of noise and the legal requirement for annual hearing tests? 员工是否知道噪声对健康的影响？是否知道法律法规要求一年做几次听力测试？ | 提问员工回答良好
|  | 5.6.6.2 When working with acids and bases, employees must wear acid and alkali resistant clothes and wear acid and alkali resistant gloves and glasses. Operation departments are responsible for maintaining the eye wash and emergency shower facilities on the production site. It is required to test the eyewash and emergency shower facilities once per week and to make regular inspection records (See HYBN-T7-08-4004-2024-1 Template of Eyewash and Emergency Shower Inspection Records). 接触酸碱操作时，岗位员工必须穿好防酸碱服，戴好防酸碱手套和眼镜。运行部门负责维护生产现场的洗眼器和水喷淋设施，要求至少每周一次对洗眼器和水喷淋设施进行测试，并做好定期检查记录工作 (见HYBN-T7-08-4004-2024-1洗眼器喷淋系统检查表)； | Check eyewash inspection records. 检查现场洗眼器工况及喷淋情况和部门检查记录。 Do employees know the monitoring frequency? 询问员工是否知道检查频次 | 提问员工回答良好
|  |  | 质检部洗眼器过滤网上积聚残留物，导致喷嘴堵塞。 | 洗眼器出水口通畅
|  | 5.6.7.1 Each operating department is responsible for the management of illumination in each workplace. Timely contact electrical department when lighting is insufficient. 每个运营部门负责管理每个工作场所的照明。照明不足时及时联系电气部门。 | Check illumination in each field operating room 检查外操室的照明 | 照明灯及手电筒完好备用
| Medical aid 医疗救护 | 5.8.1.1 First aiders will be provided with an individual identification card for easy recognition on site and in each work station. Site workers must display their first aider cards in the notice board on site, while for office workers, first aider cards must be displayed at designated notice boards. 急救人员将获得一张个人身份卡，以便在现场和每个工作站进行识别。现场员工的急救卡需在上 岗证公告栏展示，办公楼(含检维修楼、中控楼、集控楼等)需在制定公告栏展示。 | Check whether first aider card is displayed at designated notice board and if employee always bring their first aider card 检查急救员卡是否张贴在指定的公告板上，并确认员工是否随时携带急救员卡。 | 已贴在墙上
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （2）Inside each First Aid Kit shall be equipped with inspection form to list the necessary supplies and their quantities for easy inspection and replenishment. Refer to HYBN-T7-08-4005-2024-2 Template of First Aid Booklet. 每个急救箱内都要配备急救箱检查表，列出必备的用品及其数量，以方便检查和补充，详见HYBN-T7-08-4005-2024-2急救药箱记录表。 | Whether the list of supplies is paired according to the requirements and check for inspection records 急救药箱内容是否按要求配备并检查记录 | 已按要求做好检查
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （4）Oral medicines shall not be placed in the medical kit. 口服药不得放入药箱内。 | Whether the oral medicine is also in the first aid kit. 口服药是否也在急救药箱中 | 口服药不在药箱中
|  |  |  | 气防柜检查良好，加氢夜班反映空瓶四个，加裂三班及时更换 |  | 加3分 |  | 加裂三班 | 刘俊隆 | 毛奕清
|  |  | 灵活焦化外操室有4包滤毒盒和6个半面罩已超过使用有效期。重整外操室(FAR3)急救药箱内存有口服药及过期医用手套。 | 药品全部在有效期内且放在药箱外，面罩合格
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （5）The position of the medical kit shall be clear and visible indoors and there shall be a position indicator. The medical kit must not be locked and should be easily accessible during work. 医药箱位置在室内清楚可见，有位置标识指示，医药箱不得上锁并在工作期间易于取用。 | Check whether first aid kit has proper signage and indicator, if first aid kit is accessible or not 检查急救箱是否有正确的标识和指示，并确认急救箱是否易于取用 | 状态正常
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （6）Operating departments shall appoint department first aiders to check the condition of the first aid kit, quality and validity of the medicines once per month. If the medicines are inadequate or expired, such persons shall timely report to the HSE Dept. to apply for procurement, replenishment and replacement in time. 运行部门指定部门急救人员每月对急救药箱情况、药物的质量、有效期进行检查，不足或过期时 应及时向 HSE 管理部申请购买，及时补充、更换。 | Whether the first aid kit is checked regularly by department first aiders, whether the use record and the check record are complete 药箱是否被部门急救人员定期进行检查，使用记录及检查记录是否完整 | 检查合格
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.1 Education training requirements 教育和培训要求 | 5.10.1.2 All departments shall be responsible for preparing and implementing their own annual HSE education and training plans and establishing HSE training records. 各部门负责编制和实施本部门HSE年度教育和培训计划、建立HSE教育培训档案与HSE培训台帐。 | 按年度计划进行培训并存档
|  |  | 5.10.1.3 Personnel who have not passed the HSE training and examination shall not be employed. The eligibility criteria are that the test score exceeds 80% of the total score on the paper. 未经HSE培训考核合格的人员不得上岗。合格标准为考试分数超过卷面总分的80%。 | 上岗员工的安全考试成绩均为80分以上
|  | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.1 New employees in operation positions shall receive 3 level HSE training, the time is 72 academic hours, and the annual refresher training time is not less than 20 academic hours, and they can only take the post after passing the examination. 生产操作岗位新员工应接受三级HSE培训，时间为72学时，每年再培训时间不少于20学时，并经考试合格后方可上岗。 | 已按要求落实
|  | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.3 Employees subject to occupation mobility or job transfer or leaving their posts for more than six months shall receive HSE training at levels of operation dept. and team. 员工在公司内工作调动、转岗以及脱离岗位六个月以上者，应进行运行部、班组级HSE培训，经考试合格后方可上岗。 | 已按要求执行
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.4 When the operation department adopts new processes, new technologies, new materials or uses new equipment, it shall conduct targeted safety training for the relevant employees. 运行部采用新工艺、新技术、新材料或者使用新设备时，应当对有关从业人员进行针对性的安全培训。 | 如有涉及将按要求执行
|  | 5.10.5 Team-based HSE activities 班组 HSE 活动 | 5.10.5.1 All departments shall conduct department-based and team-based HSE activities. 各部门应开展以部门、班组为单位的HSE活动。 | 本月副班培训已全部完成
|  |  | 5.10.5.2 Group HSE activities shall be studied intensively at least once a month, and the learning time shall not be less than 2 academic hours each time. The department's HSE activities shall be conducted once a month, with no less than 1 academic hour each time. 班组HSE活动每月集中学习不少于一次，每次学习时间不少于2学时。部门HSE活动每月1次，每次不少于1学时。 | 已按要求完成培训
|  |  | 5.10.5.3 HSE Management Department shall formulate HSE activity learning plan of team and group every quarter. On the basis of meeting the requirements of the company, each department may arrange the learning of production process safety management knowledge, emergency drills and other HSE related activities. HSE管理部每季度制定班组HSE活动学习计划。各部门在满足公司要求的基础上，可安排生产过程安全管理知识学习、应急演练及其他与HSE相关的活动。 | 按要求开展
|  | 5.10.5 Team-based HSE activities 班组 HSE 活动 | 5.10.5.4 HSE activities of the team shall be recorded in detail in the team HSE activity record, including personnel attendance, learning records, etc. 班组HSE活动情况应在班组HSE活动记录上详细记录，包括人员出勤、学习记录等内容。 | 加裂二班签名未完成 |  | 不考核 |  |  |  | 毛奕清
|  |  | 抽查XXX班组《班组HSE活动学习记录》记录不规范，2024年12月12日班组记录，XXX未参加活动，未参加人员原因未填写。 | HSE活动记录本加氢加裂三班四班本月未记录
|  |  | 5.10.5.5 The department leader shall check the learning status of the team and sign the activity record book before the 10th of each month. The management personnel of HSE department shall conduct spot checks on HSE activities from time to time. 部门领导应对班组学习情况进行检查，并于每月10号前在活动记录本上签字，HSE部管理人员不定期对HSE活动情况进行抽查。 | 已按要求完成
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.6 HSE training for contractors and visitors 承包商及访客HSE 培训 | 5.10.6.1 Before contractor personnel enter the factory, the HSE Management Department will conduct Level I HSE training. Before entering the operation area of each unit, the Operation Department will conduct Level II HSE training. After the training, the contractors must pass the examination and conduct safety briefings before operation. Each operating department should keep training records. 承包商人员入厂前由HSE管理部实施一级HSE培训，进入各装置区域作业前由运行部实施二级HSE培训，培训结束经考试合格，作业前进行安全交底后方可作业。各运行部门应做好培训记录。 | 前期入场承包商培训记录完好
|  |  | 5.10.6.2 Visitors shall handle entry permits only when they have received entry training. 访客经入厂培训后方可办理入厂通行证。 | 后续涉及将按要求执行
|  | 5.10.6 HSE training for contractors and visitors 承包商及访客HSE 培训 | 5.10.6.3 Before the contractor and visitors enter the company, the reception department shall submit the corresponding safety training process from OA, and carry out the on-site training after receiving the approval. The contractor safety training should be applied for three days in advance, and the accurate information of the contractor personnel should be attached. 承包商及访客进入公司前，接待部门需从OA提交相应的安全培训流程，经批复后开展入厂培训。其中承包商安全培训需提前三天申请，并附承包商人员准确信息。 | 后续涉及将按要求执行
| Identification and evaluation of environmental factors 环境因素识别与评价 | 5.2.2.2 All relevant departments shall organize the personnel to identify the environmental factors that can be controlled or are expected to be exerted influence on from their activities, products and services, and to fill out the Form for Identification and Evaluation of Environ-mental Factors and feed it back to the HSE Dept. 各相关部门组织人员从其活动、产品、服务中识别出能够控制或可望施加影响的环境因素，填写《环境因素识别和评价表》并反馈到HSE管理部。 | Ask the department staff on the spot whether they are clear about the concept and identification of environmental factors, etc. 现场询问部门人员是否清楚环境因素概念及识别等 | 提问员工回答良好
|  | 5.2.7 Update of environmental factors 环境因素的更新 In case of any major change on the Company’s activities, products and services or any up-date of regulations and other requirements, all departments shall timely supplement and identify environmental factors and report to the HSE Dept. for evaluation of environmental factors to redefine the major environmental factors and conduct management on them. 当公司的活动、产品、服务发生较大变化或法规及其他要求更新时，各部门应及时对环境因素进行补充识别，并报HSE管理部进行环境因素评价，以重新确定重要环境因素并对其进行管理。 | Whether to carry out the environmental factor identification and evaluation work of the department in the current year, and whether to update the environmental factor identification and evaluation table and the list of major environmental factors in a timely manner 是否开展本部门当年度的环境因素识别和评价工作，是否及时更新环境因素识别和评价表和重要环境因素清单 | 环境因素识别已完成并上交
|  |  | Check whether the site is implemented according to the department's environmental factor list and the measures formulated 对照部门环境因素清单及制定的措施检查现场是否落实 | 已按要求落实
|  | 5.9.1.1 A comprehensive identification of environmental factors shall be carried out for device startup and shutdown as well as maintenance. 装置开、停工、检修应进行全面的环境因素识别。 | 1. Whether environmental factors are identified during the start-up, shutdown and maintenance of the device, and corresponding control measures are formulated. 2. Whether various control measures are implemented as required. 1.是否对装置开、停工及检修过程进行环境因素识别，并制定相应控制措施。 2.是否按要求落实各项控制措施。 | 已按要求做好识别
| Wastewater management 废水管理 | 5.3.1.1 All kinds of waste water must be tested to satisfied department control limit indicators formulated by the Company before discharge. 各类废水须经检测达到公司制定的分级控制指标后方可排放。 | 1. Whether the test is carried out in accordance with the annual environmental monitoring plan. 2. Check LIMS to see whether the discharge is carried out after the test results of the graded control indicators meet the standards, and whether the discharge does not meet the standards and whether to apply for abnormal discharge. 1.是否按照年度环境监测计划进行检测。 2.查LIMS，分级控制指标检测结果是否达标后排放，不达标外排是否申请异常排污。 | 含油污水化验分析登记正常。
|  | 5.3.1.6 Water Body Pollution Emergency Plan and Oil Spill Response Plan shall be prepared. 应当编制水体污染与溢油应急预案。 | 1. Whether the responsible units of each sewage outlet have formulated a plan to prevent water pollution and conduct regular drills. 2. Whether the Port and Reserve Department has prepared an oil spill emergency plan and conducted regular drills. 1.各污水外排口责任单位是否制定防水体污染预案，并定期演练。 2.港储部是否编制溢油应急预案，并定期演练。 | 已制定防污水污染预案
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 2）The operation department.: the drainage management system of the unit; the operation specifications and internal control process indicators; the diagram of drainage pipe network of the department (including: the layout of discharge point, discharge direction, the identifi-cation of sampling port, the pipe network for diverting wastewater from clean water, etc.) ; establish the waste water management ledger, etc. 运行部：本单位排水管理制度；操作规程、内控工艺指标；本部门排水管网图（应包括：排放点布置、排放去向、采样口标识、清污分流管网等）建立废水管理台帐等。 | 查资料： 1. Sewage discharge management system 污水排放管理制度 2. Drainage network diagram 排水管网图 3. Internal control process indicators 内控工艺指标（仅限在线分析仪表） 4. Wastewater management ledger 废水管理台账 | 三废管理细则已放置于外操室，员工清楚内容
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （3）Sewage treatment plants, sour water stripping units, etc. shall be in strict compliance with the operation specifications to ensure the up-to-standard discharge. 污水处理场、酸性水汽提等装置应严格遵守操作规程，确保达标排放。 | 1. Spot check whether the key operations of sewage treatment plants and acid water stripping devices have formulated operating procedures. 2. Spot check and verify whether the operations and indicator controls of each position of the team are carried out in accordance with the operating procedures. 1.抽查污水处理场、酸性水汽提装置的关键操作是否制定操作规程。 2.抽查、验证班组各岗位操作及指标控制是否按操作规程执行。 | 已按要求执行
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （5）All departments shall ensure that the drainage process is complete and in compliance with the requirements. It is forbidden to change the direction of pollution discharge without permission, and the drainage process may not be altered at will without approval. 各部门应确保排水工艺完整与符合要求，杜绝私自改变排污去向，未经批准不得随意变更排水工艺。 | Check whether the change in drainage process is carried out in accordance with the change management requirements and check the relevant change information. 变更排水工艺是否按变更管理要求执行，查相关变更资料。 | 暂无此方面变更
|  | 5.3.2.1 （20）Where the high-concentration waste water (such as the highly sulfur-containing, am-monia-containing, phenol-containing, acid-base sewage, etc.) needs to be discharged, the water volume and water quality shall be reported to the Scheduling & Dispatch Dept. and HSE Dept. and the downstream processing plant shall be contacted and given explanation about the situation at the same time to avoid impact on the sewage treatment plant. 高浓度废水（如高含硫、含氨、含酚、酸碱等污水）需排放时，应向计划调度部、HSE管理部报告水量、水质情况，同时与下游处理装置联系、说明情况，避免冲击污水处理场。 | Check the discharge of overlimt wastewater, and check the OA process of discharge. 检查超标废水产生情况，检查超标废水排放OA流程。 | 无废水超标情况
|  | 5.3.2.1 （21）All water discharged to the external environment must be analyzed to prove qualified before being discharged outwards. 所有排往外环境的水须经分析合格后方可外排。 | 1. Whether the water discharged to the external environment is sampled and analyzed according to the environmental monitoring plan. 2. Whether the monitoring items and monitoring frequency are implemented as required. 3. Whether abnormal analysis results are reported immediately and the causes of abnormalities are analyzed. 1.排往外环境的水是否按环境监测计划取样分析。 2.监测项目和监测频次是否按要求执行。 3.分析结果异常是否立即报告，并对异常原因进行分析。 | 无异常
|  | 5.3.3.6 The comparison between online monitoring data and manual monitoring data shall be conducted no less than once every quarter for the water quality online monitoring system. No unit or individual may dismantle, idle or alter the automatic monitoring equipment for pollution source. 水质在线监控系统每个季度应开展不少于1次的在线监测数据与人工监测数据的比对。任何单位和个人不得擅自拆除、闲置、改动污染源自动监测设备。 | 1. Whether the online monitoring data of the water quality online monitoring system is compared with the manual monitoring data every quarter, and check the comparison report or record. 2. Check the maintenance record of the water quality online monitoring system to see whether the calibration and maintenance are completed as required. 3. Check the integrity of the automatic monitoring equipment for sewage water quality and whether it has been dismantled, idled or modified. 1.每季度是否对水质在线监控系统开展在线监测数据与人工监测数据比对，查比对报告或记录。 2.查水质在线监控系统维护记录，是否按要求完成校验、维护。 3.查污水水质自动监测设备完好性，是否被拆除、闲置或改动。 | 已按要求登记
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.1 Regularly inspect the FGS system, evaluate the operating status of the system,record key parameters, compare historical data, and analyze the stability and performance of the system.定期对 FGS 系统进行检查，评估系统的运行状态，记录关键参数，对比历史数据，分析系统的稳定性和性能 5.3.3.2 Regular software updates and virus scans to ensure system security 定期进行软件更新和病毒扫描，确保系统安全性 | Whether the FGS system is checked regularly to ensure stable system performance, whether the software is updated and virus scanned regularly to ensure system security, and whether relevant records are complete. 是否定期对FGS系统进行检查，确保系统性能稳定，定期对软件进行更新和病毒扫描，确保系统安全性，相关记录是否齐全。 | 记录齐全
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.3 Clean the dust on the surface of the equipment in time to ensure good heat dissipation of the equipment; check the integrity of the power cord and connecting cables to prevent failuredue to aging or damage 及时清理设备表面灰尘，确保设备散热良好；检查电源线和连接电缆的完好性，防止因老化或破损导致故障 | Check and maintain the equipment to ensure the integrity of system components and check whether maintenance records are complete. 是否对设备进行检查和保养，确保系统部件性能完整，检查保养记录是否齐全 | FGS未出现故障
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.4 When a system failure occurs, the possible cause of the failure is determined based on the failure phenomenon, and corresponding troubleshooting measures are taken promptly to ensure the stable operation of the system. 当系统出现故障时，根据故障现象判断可能的故障原因，及时采取相应的故障排除措施，保障系 统的稳定运行。 5.3.3.5 Regularly conduct comprehensive calibration and debugging of the system to ensure the accuracy of various parameters and eliminate errors caused by long-term operation 定期对系统进行全面校准和调试，确保各项参数准确，消除因长期运行导致的误差。 | Whether the fault is promptly eliminated when it occurs, whether the system is fully calibrated and debugged regularly to ensure that all parameters are accurate, and whether the maintenance records are complete; 是否在出现故障时，及时排除故障，是否定期对系统进行全面校准和调试，确保各项参数准确，维修记录是否齐全； | FGS未出现故障
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.6 Establish and improve system maintenance work records, including inspection content, fault diagnosis, component replacement and other information, and organize and archive them to facilitate subsequent inquiries and analysis. 建立健全系统维修保养工作记录，包括检查内容、故障诊断、部件更换等信息，并整理归档，便于后续查询和分析。 | Whether a sound maintenance record has been established and whether the record content is complete; whether monthly work suggestions are made for the system operation. 是否建立健全维修保养记录，记录内容是否完整；是否对系统运行情况提出月度工作建议。 | 记录完整
| 5.5 Fire prevention inspections and hidden danger management 消气防监督检查和隐患治理 | 5.5.2 Rectification of hidden dangers 隐患整改 For the hidden dangers spotted during the fire inspection, the department concerned shall contact corresponding department and personnel for to tackle with them. Rectification of ordinary hidden dangers shall be performed by professionals organized by each department. Major hidden dangers shall be rectified after the discussion by HSE management committee, before which safety protection measures shall be implemented by the personnel of relevant departments. 对于防火检查中发现的隐患，由所在部门联系相关部门和人员进行处理。一般隐患由各部门组织专业人员进行整改；重大隐患经公司HSE管理委员会讨论后落实整改，整改前由有关部门人员落实安全防护措施。 | Whether hidden dangers found during fire prevention inspections have been rectified in a timely manner; whether problems that have not been rectified in a timely manner and major hidden dangers have been included in the hidden danger ledger and reported to the HSE Management Department in a timely manner. 防火检查中发现的隐患，是否及时落实整改；未及时落实整改的问题及重大隐患是否列入隐患台账，并及时上报HSE管理部。 | 已全部签字
|  |  | 加氢三班演练：15：46工艺演练开始。15：48确认原因后汇报部门领导。16：02发现有人中毒。16：03疏散人员。16：04内操报警，远程切断。16：05确认后汇报部门领导。16：06 用吸油毡。16：08抬走伤员。16：09人员打开消防炮时空呼脱落，16：09接车16：11找到伤员，控制现场16：12关闭阀门进行环保处理，16：18呼叫检修，演练结束。 | 加氢三班演练不足：1、伤员在下风向，操作消防炮时候面罩脱落。2、接车人伤员位置汇报错误。3、环保处理未封堵雨水沟 |  |  |  | 加氢三班 |  | 毛奕清
|  |  | 加裂三班演练：11：45工艺注水中断演练开始。11：55外操汇报加裂P215B机封大量泄漏石脑油，中控班长立刻拨打火警电话并远传停泵，关阀隔离；外操班长安排现场人员到现场处置；11：57分人员到达泄漏现场，使用消防设施对泄漏点喷水掩护。12：02消防队到达现场水幕掩护配合处置，直至演练结束，班组员工清理地面油污并检查雨水系统油污情况。 | 加裂三班演练不足：1、人员进入泄漏现场处理过程未背带空呼；2、消防水消防炮没尽可能利用 |  |  |  | 加裂三班 |  | 江志宁

## 日检表 (19)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期：11 MM 19 DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分装置内动火, 界区外穿管和动火.动火前地沟未覆盖，警戒区域设置不合理。 |  | 扣2分 | 2025-11-19 | 加裂四班 | 袁茂波 | 毛奕清
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽考安华未答出 |  | 扣2分 | 下个白板再次抽考 | 加氢四班 | 安华 | 毛奕清
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  | 加氢四班演练过程：14：01工艺演练开始14：05汇报领导，未提及疏散。14：20现场发生泄漏。组织疏散。14：21内操切断泄漏点。开始报警。14：23泄漏点关闭阀门，伤员抬到下风向。14：25接车，伤员位置描述明确。14：26消防队进入。控制泄漏，伤员抬上救护车。14：26汇报部门领导现场有伤员。14：29演练结束 | 不足：：1、未第一时间汇报领导，事后未环保处理。2、抬人方式不对，人员坠地。3、两人在下风向区域活动。 |  |  |  | 加氢四班 |  | 毛奕清
|  |  | 加裂四班演练：11：45工艺注水中断演练开始。11：54外操汇报加裂P215B机封大量泄漏石脑油，中控班长立刻拨打火警电话并远传停泵，关阀隔离；外操班长安排现场人员到现场处置；11：57分人员佩戴好空呼到达泄漏现场，使用消防设施对泄漏点喷水掩护，并就近关闭机泵前后手阀。12：01消防队到达现场水幕掩护配合处置，直至演练结束，班组员工清理地面油污并检查雨水系统油污情况。 | 加裂四班演练不足：1、中控汇报消息不准确，2、现场无着火，中控汇报有着火 |  |  |  | 加裂四班 |  | 江志宁
|  |  | 加裂二班演练：11：30工艺注水中断演练开始。11：40外操汇报加裂P215B机封大量泄漏石脑油，中控班长立刻拨打火警电话并远传停泵，关阀隔离；外操班长安排现场人员到现场处置；11：43分人员佩戴好空呼到达泄漏现场，使用消防设施对泄漏点喷水掩护，并就近关闭机泵前后手阀。11：46消防队到达现场水幕掩护配合处置，直至演练结束，班组员工清理地面油污并检查雨水系统油污情况。 | 加裂二班演练不足：1、消防水带使用的离泄漏点过近，无法将水带展开；2、没做好人员疏散，演练过程中一名检修人员在装置内穿行；3、现场消防设施没落实，就喊已完成，演练流于形式 |  |  |  | 加裂二班 |  | 江志宁

## 日检表 (18)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分装置内动火, 界区外穿管和动火.
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
|  |  |  | 15日加氢二级火票马斯鲁没做气体分析 |  | 扣2分 |  | 加氢三班 | 马斯鲁 | 江志宁
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽考赛菲克回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 柴油D502引导铁皮请保持黑色朝外，砂袋破损已考核，未修复。 |  | 扣2分 |  | 加氢一班 |  | 毛奕清
|  |  |  | 配合更换空呼气瓶 |  | 加4分 |  | 加裂一班 |  | Wafi
|  |  |  | 加氢PRC管廊下Xm11078盖上很多油污。 |  | 扣1分 |  | 加氢二班 |  | 江志宁
|  |  | 加氢一班演练过程：14：10工艺演练开始，汇报领导，人员疏散。14：26现场发生泄漏，人员中毒。14：26内操报警。14：27两人佩戴抬走伤员。14：28切断阀门，现场使用消防水，蒸汽等掩护泄漏部位。14：30路口接车。14：32伤员上救护车，班组联系检修。14：35演练结束 | 不足：1、人员疏散不到位，电气，仪表人员在演练过程中穿插。2、伤员在下风向，其他人员也处于下风向区域。3、抬人的姿势不对，演练末尾未进行环保处置。 |  |  |  | 加氢一班 |  | 毛奕清
|  |  | 加裂二班演练：11：30工艺注水中断演练开始。11：45外操汇报加裂P215B机封大量泄漏石脑油，中控班长立刻拨打火警电话并远传停泵，关阀隔离；外操班长安排现场人员到现场处置；11：48分人员佩戴好空呼到达泄漏现场，使用消防设施对泄漏点喷水掩护，并就近关闭机泵前后手阀。11：50消防队到达现场水幕掩护配合处置，直至演练结束，班组员工清理地面油污并检查雨水系统油污情况。 | 加裂一班演练不足：1.内操报警时重点信息交代不全面，泄漏介质等没汇报。2.现场消防队没到现场，中控内操反馈消防队已经接管导致路边接车人员全部撤走。3.现场蒸汽胶管开完阀后没踩住，易导致甩龙伤人；水带水炮等没使用 |  |  |  | 加裂一班 |  | 江志宁

## 日检表 (17)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 技改线脚手架作业, 技改线动火作业, 加氢C201安全阀高处作业
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
|  |  |  | 加氢C201安全阀高处作业，监护人未穿监护服。 |  | 扣2分 |  | 加氢二班 |  | 毛奕清
|  |  |  | 11月15日保温作业期间，作业监护人不在作业现场，违反作业票/高风险作业监护“全程在位”要求。 |  | 扣2分 |  | 加氢四班 |  | Wafi
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 艾哈迈德和法婷回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 泵位（1041-P103、1040-P107、1040-P211、1040-P212、1040-P106、1040-P217A、1040-P207A、1040-P105、1040-P218、1030-P101）：昨夜降雨，交接后现场发现沟内仍异常干燥，判断含油污水排水口沙袋封堵不到位；请复查沙袋状态并在沙袋下铺设塑料薄膜，确保有效封堵并确认效果 |  | 各点扣1分 | 11月24日前整改 |  |  | Wafi
|  |  |  | 1040-E102西推车XM11268卡片湿了，请保护好不要弄湿，公司会考核 |  | 不考核 |  | 加裂一班 |  | 毛奕清
|  |  |  | 1040-E102西推车XM11268卡片湿了，请保护好不要弄湿，公司会考核 |  | 不考核 |  | 加裂二班 |  | 毛奕清
|  |  |  | 1030-PA501 磷酸盐泵排水口未用沙袋封堵 |  | 扣2分 |  | 加氢一班 |  | Wafi
|  |  | 演练经过：13：59工艺演练启动，汇报领导。14：15发现泄漏，有人员中毒。14：15疏散人员。14：15报警呼叫消防队。14：16下风向布置消防水炮和蒸汽皮管。14：18佩戴空呼进入，切断阀门，救人。14：20路口接车。14：22消防队找到伤员，接走。布置现场救助协助控制泄漏区域 | 不足：1、先切断阀门，再救人。伤员未持续救治。2、未进行环保处置。 |  |  |  | 加氢二班 |  | 毛奕清

## 日检表 (14)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 柴油C201顶安全阀拆装
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽查肖斌，阿扎姆回答良好，赛菲克未答出。 |  | 扣2分 |  | 加裂一班 | 赛菲克 | 毛奕清
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 1030-K101B地面服务站缺少胶垫，附近无备件 |  | 扣2分 |  | 加氢一班 |  | 毛奕清
|  |  |  | 1040-E205平台西南角编号XM11490,XM11491,XM11493 褪色严重 |  | 扣1分 |  | 加裂一班 | 穆尼 | 毛奕清

## 周检表 (13)
HSE Weekly Checklist for No.2 Refining Department 炼油二部HSE周检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
| Safety Management System 安全管理制度 5.3 HSE hidden danger identification HSE 隐患排查 | 5.3.3.6 All departments shall prepare hidden danger identification form based on their discipline characteristics and actual production conditions and continue to improve such form in practice. 各部门应根据专业特点和实际生产情况制定隐患排查表，并在实际应用中不断持续改进。 5.3.4.1 Control requirements 治理要求 （1）For general hidden danger, departments involved shall immediately organize rectification. 对于一般隐患，由属地所在部门立即组织整改。 （2）For any general hidden danger which can’t be rectified immediately, the department involved shall develop a risk precaution plan and rectification plan, and rectify such danger within a specified timeframe. 对于暂不能整改的一般隐患，由属地部门制定风险防范措施和整改计划，限期整改。 5.3.6.1 All departments shall establish Hidden Danger Identification & Control Account. 各部门应建立《隐患排查治理台账》。 5.3.6.2 The hidden danger treatment should be recorded according to the "HSE Hidden Danger Investigation and Management Ledger" to achieve closed-loop rectification. 隐患治理情况应按《HSE 隐患排查治理台账》进行记录，做到闭环整改。 | Does the hidden danger investigation table meet the investigation requirements 隐患排查表是否满足排查要求 | 加氢11月隐患27个，加裂12月隐患66个，12月隐患5个
|  |  | Whether the hidden danger investigation and management record is updated in time 隐患排查治理台账是否及时更新 | 已更新至最新版本
|  |  | Whether all staff are trained on hidden danger management 是否组织全员培训隐患治理情况 | 列入每月副班培训中
|  |  | Is the rectification carried out as planned 是否按计划整改 | 有条件的将立即整改
加裂炉子附近进料流量计搭架子
手机及上岗证已按要求上墙
| Safety Management System 安全管理制度 5.4 Management of hazardous chemicals 危险化学品管理 | 5.4.2.2 The HSE management department shall supervise the establishment of hazardous chemicals ledger by all departments.. HSE 管理部监督各部门建立危险化学品台帐。 5.4.2.4 Each operation department must carry out targeted training on the knowledge of hazardous chemicals according to the hazardous chemicals involved in its own department,and staff shall be familiar with information on safety technology of hazardous chemical involved in the post to ensure stable operation and personal safety in production, storage, use, transportation and disposal of hazardous chemicals. 各运行部必须根据本部门涉及的危险化学品开展针对性的危险化学品知识培训，建立本部门《化学品普查表》与《危险化学品台帐》。员工应熟悉本岗位涉及的危化品安全技术信息，以保证危险化学品生产、储存、使用、运输、废弃处置等环节的平稳操作和人身安全。 5.4.2.5 Before using hazardous chemicals, the staff must know and grasp relevant MSDS andsafe operation instructions of hazardous chemicals, take relevant precautionary measures and prevent personal injuries. 员工使用危险化学品时，必须了解和掌握相应危险化学品安全技术说明书和安全操作规程有关内容，并采取相应的防范措施，避免发生人身伤害事故。 | Does the department have a hazardous chemicals register 部门是否建立危险化学品台账 | 已更新至最新版本（二部危化品台账）
|  |  | Whether to organize full-staff learning 是否组织全员学习 | 已放在外操室电脑供学习
| Safety Management System 安全管理制度 5.14.Hydrogen sulfide prevention 防硫化氢中毒安全管理 | 5.14.1 All departments shall set up eye-catching warning signs in both Chinese and English in places where hydrogen sulfide leakage may occur, and hydrogen sulfide warning signs shall be set up in eye-catching places in workplaces where hydrogen sulfide exists. A wind vane shall be set in the eye-catching position of the unit. 各部门在可能发生硫化氢泄漏的场所设置醒目的中英文警示标识，存在硫化氢的工作场所应在醒目位置设置硫化氢告知牌。装置醒目位置应设置风向标。 5.14.2 All personnel having access to hydrogen sulfide hazard area shall carry portablehydrogen sulfide alarms and protection devices as required. 所有进入可能存在硫化氢等有毒有害气体区域的巡检或作业的人员，必须佩戴相应的便携式气体检测仪和防护器具。集中作业时，作业小组应至少佩戴 1 台便携式气体检测仪。 5.14.3 The site concentration should be monitored at any time when the acid water, gas escape site, drain port, sampling port, storage tank metering port and other hidden parts are active. 在酸性水、瓦斯逸出部位、排液口、采样口、储罐计量口等隐患部位活动时，应随时监控现场浓度。 5.14.4 When entering hydrogen sulfide hazard area for patrol, operators shall conduct individual protection well and carry portable hydrogen sulfide alarm. In case of operation in hydrogen sulfide hazard area, it shall wear isolated respirator, set up warning signs around operation points and assign special personnel for monitoring. 员工在涉及接触硫化氢等有毒有害气体作业时，应做好个体防护，佩戴便携式气体检测仪和适宜呼吸防护用品，并有专人进行监护。 5.14.5 According to the working environment of different posts, all departments shall equip the operators with appropriate protective equipment. When the concentration of hydrogen sulfide is less than 50mg/m3, filter type anti-gas appliances can be used; When the hydrogen sulfide concentration is greater than 50mg/m3 or in the area where the medium leakage occurs and the concentration is unknown, isolated respiratory protective equipment should be used,and the gas supply device of the protective equipment should be placed on the upwind side. 各部门根据不同岗位的工作环境为作业人员配备适量适用的防护器材。当硫化氢浓度低于50mg/m3 时，可以使用过滤式防毒用具；当硫化氢浓度大于 50mg/m3 或在发生介质泄漏、浓度不明的区域内应使用隔离式呼吸防护用具，防护用具的供气装置应置于上风侧。 5.14.6 It is forbidden for any person to enter the area where hydrogen sulfide poisoning may occur without proper protective equipment, and it is forbidden to take off the protective equipment in the toxic area. 禁止任何人员不佩戴合适的防护器具进入可能发生硫化氢中毒的区域，禁止在有毒区内脱卸防毒用具。 5.14.7 When the hydrogen sulfide detection instrument alarms, the panel operator should remind the site personnel in time, the operator should wear protective equipment, check the leak point, prepare protective equipment and report to the superior, and evacuate the downwind personnel, prohibit all fire operations, quickly identify the cause of the leak and control the leak. 硫化氢检测仪器报警时，内操应及时提醒现场人员，作业人员应佩戴防护用具、检查泄漏点、准备防护用具并向上级报告，同时疏散下风向人员，禁止一切动火作业，迅速查明泄漏原因并控制泄漏。 5.14.8 Operation in hazardous places that may contain hydrogen sulfide, such as sewage wells and closed containers, shall be carried out in strict accordance with the management requirements of restricted Spaces of this system. 进入污水井、密闭容器等可能含硫化氢的危险场所作业，要严格按照本制度受限空间的管理要求执行。 5.14.9 When construction and maintenance personnel of contractors enter hydrogen sulfide hazard area to work, operation departments where they belong to shall organize construction contractors to conduct risk identification and notification of hydrogen sulfide hazards in operation area, and provide necessary protective devices and emergency rescue facilities. 承包商作业人员在涉及硫化氢等有毒有害气体环境中作业时，属地部门应对承包商作业人员进行硫化氢等有毒有害气体防中毒防窒息安全培训和安全交底，为其提供必要的呼吸防护器具和应急救护设施如正压式呼吸器，长管呼吸器等。 5.14.10 Any operator which is likely to come in contact with poisonous and harmful gases such as the hydrogen sulfide shall take trainings on poisoning and suffocation prevention and shall only take the job after being tested to be qualified. 凡可能接触硫化氢等有毒有害气体的操作人员，应接受防中毒、防窒息安全教育，经考核合格，方可上岗操作。 5.14.11 Departments that may have hydrogen sulfide leakage shall formulate emergency rescue plans and establish a first aid network, ensure that on-site first aid, evacuation and escort, and transport rescue channels are unblocked, conduct regular drills on emergency plans, and revise and improve them in time. 可能存在硫化氢泄漏的部门要制定应急救援预案并建立急救网络，保证现场急救、撤离护送、转运抢救通道畅通，对应急预案定期进行演练，并及时进行修订完善。 | Have employees been trained to prevent hydrogen sulfide poisoning 是否对员工进行防硫化氢中毒培训 | 已全员考试验收
Comprehensive Management 综合管理 | 5.2 HSE organization HSE 组织机构 | 5.2.2 Each department shall establish a safety management organization and establish the corresponding HSE Organization Ledger 各部门应建立安全管理组织机构，并建立相应的《HSE组织台帐》 | Whether the Organizational Ledger has been established and updated in a timely manner 是否建立了组织机构台帐，是否及时进行了更新 | 组织机构台账已建立，更新及时.
| 5.3 HSE policies and objectives HSE方针 | People-oriented, compliance with laws and regulations, community harmony, environmentfriendly, risk controllable. 以人为本、依法合规、社区和谐、环境友好、风险可控。 | Are employees clear about the company's policies, goals and commitments? 员工是否清楚公司方针目标与承诺 | 提问员工回答良好
| 5.4 HSE commitment HSE承诺 | 5.4.1 Abide by Brunei's laws and regulations, respect local customs and habits, and maintain a consistent attitude towards HSE in all business areas. 遵守文莱法律、法规，尊重当地风俗习惯，在所有业务领域对HSE的态度始终如一。 5.4.2 Care for life and health, protect the ecological environment, always adhere to zero tolerance for violations, and pursue the goal of zero injury, zero pollution, and zero accidents. 关爱生命健康，保护生态环境，始终坚持违章零容忍，追求零伤害、零污染、零事故的目标。 5.4.3 In order to ensure the achieve the goal, provide human, material and financial resources to support. 为保证目标的实现，提供人力、物力和财力等资源支持。 5.4.4 Regularly report HSE performance to the Brunei government, account for the needs of stakeholders such as investors, customers, and contractors, and actively accept supervision from all parties around us to achieve continuous improvement. 定期向文莱政府公布HSE业绩，关注投资者、客户、承包商等利益相关方需求，主动接受社会各界监督，实现持续改进。 | Are employees clear about the company's policies, goals and commitments? 员工是否清楚公司方针目标与承诺 | 提问员工回答良好
| 5.9 HSE meeting HSE 会议 | 5.9.2.3 Each department holds a regular HSE meeting once a week. 各部门 HSE 例会每周召开一次。 5.9.3.3 HSE regular meeting of each department 各部门 HSE 例会 （1） Communicate the requirements of HSE meetings at all levels of the company and the recent safety production situation of the company. 传达公司各级 HSE 例会的要求及近期公司安全生产形势。 （2） Arrange HSE work of the department, and solve HSE related problems in the work of each team and staff. 布置本部门 HSE 工作，解决各班组及员工工作中 HSE 相关问题。 | The content of the company's HSE regular meeting was carefully communicated. The HSE regular meeting of this department was held on time. 公司HSE例会内容认真传达 本部门HSE例会按时召开 | 公司例会内容交接班时进行宣贯，并将例会纪要发到群里；部门例会每月末按时召开
| 5.14 HSE assessment HSE考核 | 5.14.2 Each department shall refer to the Company's "Performance Appraisal Measures" or refine the performance appraisal system of its own department to assess, reward and punish the HSE work of its own department, and establish the HSE assessment reward and punishment ledger. 各部门引用公司《绩效考核办法》或细化为本部门绩效考核制度，对本部门的HSE工作情况进行考核奖惩，并建立 HSE 考核奖惩台帐。 | Department’s HSE assessment status 部门的HSE考核情况 | 已在日周月检表内体现
Comprehensive Management 综合管理 | 5.16 Accident and incident management 事故事件管理 | 5.16.4.1 Each operation department shall encourage its employees to report near-miss accidents, and organize investigations and analyses on the near-miss accidents to find out the root cause and prevent the reoccurrence of the accidents. 各运行部门应鼓励并奖励员工报告未遂事件，并组织对未遂事件进行调查、分析，找出事故根 源，预防事故发生。 | Did the department make any request on reporting nearmiss incident? 部门是否对未遂事件进行过要求 | 本周没有未遂事件
|  | 5.16.5.1 incident and accident management requirements 事故、 事件报告要求 After an operation department accident or incident occurs, the occurrence department shall immediately report to the dispatch room, the person in charge of the department and the HSE Management Department, and submit a Preliminary Report Form of Accident (Incident) to the HSE Department via email within 24 hours. 发生事件、运行部级事故后，发生部门应立即报告调度室、本部门负责人和 HSE 管理部， 24 小时内通过邮箱向 HSE 管理部提报《事故（事件） 初步报告表》。 | Whether departmental accidents have been reported as required 部门事故事件是否按要求进行了报告 | 本周无事故事件发生
|  | 5.16.6.1 Incident investigation 事件调查 Where the incident submitted to the "Accident (incident) Preliminary Report Form", the occurrence department shall organize the incident investigation within one week after the occurrence of the incident, prepare the incident investigation record form, and the department shall file the record. 凡提报《事故（事件）初步报告表》的事件，发生部门应在事件发生后一周内组织事件调查，编写《事故（事件） 报告表》 ， 报 HSE 管理部。 | Whether the department's accident incidents are investigated as required 部门事故事件是否按要求开展调查 | 本周无事故事件发生
|  |  | 事故事件台帐已经建立，台帐内容填写不全，维护不及时。 | 事故事件台账已完善
|  | 5.16.7.1 In the course of handling of accidents and incidents, the principles of “Four do not let go”, namely, not allowing any existence of unclear accident causes, not allowing any missing of punishment on accountable parties of the accident, not allowing any failure in implementing the rectification measures and not allowing any failure in mass education targeting relevant liable personnel. 事故、事件处理都要坚持“四不放过”原则，即事故原因未查清不放过、责任人员未处理不放过、整改措施未落实不放过、有关人员未受到教育不放过。 | For accidents in the department, has the department adhered to the "Four Do No-Let-Go" principle? For accidents in other departments of the company, has the department organized employees to learn? 对于部门的事故，部门是否坚持了四不放过原则，对于公司其他部门的事故，是否组织了本部门员工进行学习 | 本周无事故事件发生
|  | 5.5.2.3 Issuance of protection supplies 防护用品发放 （1）The operation department must, according to the requirements of work safety and prevention of occupational hazards, issue to employees PPE with different protection functions and record the issuance of PPE according to “One Person One Record” (See HYBN-T7-08-4001-2024-3 Template of PPE Issuing Records); 运行部门必须根据安全生产和防止职业性危害的需要，发给员工具有不同防护功能的劳动防护用品并按照“一人一卡” 做好劳动防护用品发放记录（参照HYBN-T7-08-4001-2024-3劳动防护用品发放记录模板）; | Whether to establish an employee PPE distribution ledger, whether the ledger is true and complete. 是否建立员工PPE发放台账，台账是否真实、完整。 | 台账已按要求建立，检查没问题
|  |  | XXX部有劳保发放记录但未建立“一人一卡。要求部门按照“一人一卡”劳保发放记录落实。 | 按照一人一卡落实
|  | 5.6.3.1 Operation protection 作业防护 （1）Prior to operation, workplaces where toxic gases may be present shall be tested for toxic gas concentration; 作业前对可能存在有毒气体的工作场所进行有毒气体浓度检测； | Do employees know which toxic and hazardous gases are present in their department and the required protective equipment? 员工是否知道部门有哪一些有毒有害气体？是否懂需要用什么劳动防护用品？ Does management have a list of hazardous substances/MSDS list? Has it been shared to employees? Do employee know how to read/obtain information from a MSDS? 管理人员是否建立部门内部的有毒有害气体清单并做好内部宣贯？员工是否了解MSDS内容？ Does employee know what does IDLH means? 员工是否知道IDLH指什么？IDLH是英文Immediately Dangerous to Life or Health concentration的缩写，指的是直接致害浓度。 | 抽查陈先容，艾哈迈德，萨吉，法婷，史文超回答良好。侯雪峰，奥黛丽，拉凯布，罗庆通， 马国淮未答出 |  | 各扣2分 |  | 加氢二班加裂二班 |  | 毛奕清
|  | 5.6.1.4 Employees who participate in poisonous and harmful operations must undergo occupational health education beforehand, keep records of Occupational Health training records (See HYBN-T7-08-4003-2024-1 Occupational Health Training Records) and be provided with effective PPE. 对参加有毒有害作业员工，必须事先进行职业健康教育，做好职业健康培训记录(见HYBN-T7-08-4003-2024-1职业健康培训档案) 并提供有效的劳动防护用品。 5.6.1.7 Occupational Health regular training materials should be recorded and accompanied with proper records (See HYBN-T7-08-4003-2024-1 Occupational Health Training Archives) and filed for storage. 职业健康专业定期学习材料应做好职业健康培训记录 (见HYBN-T7-08-4003-2024-1职业健康培训档案) 并做好存档。 | Check if training records have been established? 培训档案是否按照要求建立？ Check whether OH poster had been published and shared with employees on a timely basis and if records had been logged. 检查职业健康海报是否已及时发布并与员工分享，并查看是否有记录登记 | 本月健康简报已打印放置于外操室外墙上
|  | 5.6.2.1 Noise protection 噪声防护 （1）Employees must wear earplugs or earmuffs when they are exposed to workplaces with excessive noise (greater than 85 dB). 员工接触噪声超标 (大于85dB) 的作业场所，必须配戴防噪声耳塞或耳罩； | Are employees aware of noise exposure limits? 员工是否知道噪声超标指标？ If noise exposure exceeds limit, what should you do? 如果超标，是否知道要佩戴什么防护用品？ | 提问员工希达雅 ,萨吉和那比尔回答良好
|  | 5.6.2.2 Noise monitoring 噪声监测 （1）Conduct monitoring of noise at workplaces and noise exposure of employees semiannually; 每半年对作业场所噪声及员工噪声暴露情况至少进行一次监测； | Do employees know the internal noise monitoring points within their department? 员工是否知道部门内部噪声监测点在哪里？ | 提问员工希达雅 ,萨吉和那比尔回答良好
|  | 5.6.2.4 Hearing protection 听力保护 （1）According to local laws and regulations, employees at workplaces where there is excessive noise level of more than 85 db(A) should undergo annual audiometry testing to ascertain the impact of excessive noise exposure and to prevent long term hearing loss. 在噪音水平超过85dB(A)的工作场所工作的员工应接受年度听力测试，以确定过度噪音暴露的影响并防止长期听力损失。 | Are employees aware of the health effects of noise and the legal requirement for annual hearing tests? 员工是否知道噪声对健康的影响？是否知道法律法规要求一年做几次听力测试？ | 提问员工希达雅 ,萨吉和那比尔回答良好
|  | 5.6.6.2 When working with acids and bases, employees must wear acid and alkali resistant clothes and wear acid and alkali resistant gloves and glasses. Operation departments are responsible for maintaining the eye wash and emergency shower facilities on the production site. It is required to test the eyewash and emergency shower facilities once per week and to make regular inspection records (See HYBN-T7-08-4004-2024-1 Template of Eyewash and Emergency Shower Inspection Records). 接触酸碱操作时，岗位员工必须穿好防酸碱服，戴好防酸碱手套和眼镜。运行部门负责维护生产现场的洗眼器和水喷淋设施，要求至少每周一次对洗眼器和水喷淋设施进行测试，并做好定期检查记录工作 (见HYBN-T7-08-4004-2024-1洗眼器喷淋系统检查表)； | Check eyewash inspection records. 检查现场洗眼器工况及喷淋情况和部门检查记录。 Do employees know the monitoring frequency? 询问员工是否知道检查频次 | 提问员工回答良好
|  |  | 质检部洗眼器过滤网上积聚残留物，导致喷嘴堵塞。 | 洗眼器出水口通畅
|  | 5.6.7.1 Each operating department is responsible for the management of illumination in each workplace. Timely contact electrical department when lighting is insufficient. 每个运营部门负责管理每个工作场所的照明。照明不足时及时联系电气部门。 | Check illumination in each field operating room 检查外操室的照明 | 照明灯及手电筒完好备用
| Medical aid 医疗救护 | 5.8.1.1 First aiders will be provided with an individual identification card for easy recognition on site and in each work station. Site workers must display their first aider cards in the notice board on site, while for office workers, first aider cards must be displayed at designated notice boards. 急救人员将获得一张个人身份卡，以便在现场和每个工作站进行识别。现场员工的急救卡需在上 岗证公告栏展示，办公楼(含检维修楼、中控楼、集控楼等)需在制定公告栏展示。 | Check whether first aider card is displayed at designated notice board and if employee always bring their first aider card 检查急救员卡是否张贴在指定的公告板上，并确认员工是否随时携带急救员卡。 | 已贴在墙上
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （2）Inside each First Aid Kit shall be equipped with inspection form to list the necessary supplies and their quantities for easy inspection and replenishment. Refer to HYBN-T7-08-4005-2024-2 Template of First Aid Booklet. 每个急救箱内都要配备急救箱检查表，列出必备的用品及其数量，以方便检查和补充，详见HYBN-T7-08-4005-2024-2急救药箱记录表。 | Whether the list of supplies is paired according to the requirements and check for inspection records 急救药箱内容是否按要求配备并检查记录 | 已按要求做好检查
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （4）Oral medicines shall not be placed in the medical kit. 口服药不得放入药箱内。 | Whether the oral medicine is also in the first aid kit. 口服药是否也在急救药箱中 | 口服药不在药箱中
|  |  | 灵活焦化外操室有4包滤毒盒和6个半面罩已超过使用有效期。重整外操室(FAR3)急救药箱内存有口服药及过期医用手套。 | 药品全部在有效期内且放在药箱外，面罩合格
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （5）The position of the medical kit shall be clear and visible indoors and there shall be a position indicator. The medical kit must not be locked and should be easily accessible during work. 医药箱位置在室内清楚可见，有位置标识指示，医药箱不得上锁并在工作期间易于取用。 | Check whether first aid kit has proper signage and indicator, if first aid kit is accessible or not 检查急救箱是否有正确的标识和指示，并确认急救箱是否易于取用 | 状态正常
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （6）Operating departments shall appoint department first aiders to check the condition of the first aid kit, quality and validity of the medicines once per month. If the medicines are inadequate or expired, such persons shall timely report to the HSE Dept. to apply for procurement, replenishment and replacement in time. 运行部门指定部门急救人员每月对急救药箱情况、药物的质量、有效期进行检查，不足或过期时 应及时向 HSE 管理部申请购买，及时补充、更换。 | Whether the first aid kit is checked regularly by department first aiders, whether the use record and the check record are complete 药箱是否被部门急救人员定期进行检查，使用记录及检查记录是否完整 | 检查合格
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.1 Education training requirements 教育和培训要求 | 5.10.1.2 All departments shall be responsible for preparing and implementing their own annual HSE education and training plans and establishing HSE training records. 各部门负责编制和实施本部门HSE年度教育和培训计划、建立HSE教育培训档案与HSE培训台帐。 | 按年度计划进行培训并存档
|  |  | 5.10.1.3 Personnel who have not passed the HSE training and examination shall not be employed. The eligibility criteria are that the test score exceeds 80% of the total score on the paper. 未经HSE培训考核合格的人员不得上岗。合格标准为考试分数超过卷面总分的80%。 | 上岗员工的安全考试成绩均为80分以上
|  | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.1 New employees in operation positions shall receive 3 level HSE training, the time is 72 academic hours, and the annual refresher training time is not less than 20 academic hours, and they can only take the post after passing the examination. 生产操作岗位新员工应接受三级HSE培训，时间为72学时，每年再培训时间不少于20学时，并经考试合格后方可上岗。 | 已按要求落实
|  | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.3 Employees subject to occupation mobility or job transfer or leaving their posts for more than six months shall receive HSE training at levels of operation dept. and team. 员工在公司内工作调动、转岗以及脱离岗位六个月以上者，应进行运行部、班组级HSE培训，经考试合格后方可上岗。 | 已按要求执行
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.4 When the operation department adopts new processes, new technologies, new materials or uses new equipment, it shall conduct targeted safety training for the relevant employees. 运行部采用新工艺、新技术、新材料或者使用新设备时，应当对有关从业人员进行针对性的安全培训。 | 如有涉及将按要求执行
|  | 5.10.5 Team-based HSE activities 班组 HSE 活动 | 5.10.5.1 All departments shall conduct department-based and team-based HSE activities. 各部门应开展以部门、班组为单位的HSE活动。 | 本月副班培训已全部完成
|  |  | 5.10.5.2 Group HSE activities shall be studied intensively at least once a month, and the learning time shall not be less than 2 academic hours each time. The department's HSE activities shall be conducted once a month, with no less than 1 academic hour each time. 班组HSE活动每月集中学习不少于一次，每次学习时间不少于2学时。部门HSE活动每月1次，每次不少于1学时。 | 已按要求完成培训
|  |  | 5.10.5.3 HSE Management Department shall formulate HSE activity learning plan of team and group every quarter. On the basis of meeting the requirements of the company, each department may arrange the learning of production process safety management knowledge, emergency drills and other HSE related activities. HSE管理部每季度制定班组HSE活动学习计划。各部门在满足公司要求的基础上，可安排生产过程安全管理知识学习、应急演练及其他与HSE相关的活动。 | 按要求开展
|  | 5.10.5 Team-based HSE activities 班组 HSE 活动 | 5.10.5.4 HSE activities of the team shall be recorded in detail in the team HSE activity record, including personnel attendance, learning records, etc. 班组HSE活动情况应在班组HSE活动记录上详细记录，包括人员出勤、学习记录等内容。 | HSE活动记录本加氢加裂四个班本月未记录
|  |  | 抽查XXX班组《班组HSE活动学习记录》记录不规范，2024年12月12日班组记录，XXX未参加活动，未参加人员原因未填写。 | 班组活动记录本已全部完成记录
|  |  | 5.10.5.5 The department leader shall check the learning status of the team and sign the activity record book before the 10th of each month. The management personnel of HSE department shall conduct spot checks on HSE activities from time to time. 部门领导应对班组学习情况进行检查，并于每月10号前在活动记录本上签字，HSE部管理人员不定期对HSE活动情况进行抽查。 | 已按要求完成
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.6 HSE training for contractors and visitors 承包商及访客HSE 培训 | 5.10.6.1 Before contractor personnel enter the factory, the HSE Management Department will conduct Level I HSE training. Before entering the operation area of each unit, the Operation Department will conduct Level II HSE training. After the training, the contractors must pass the examination and conduct safety briefings before operation. Each operating department should keep training records. 承包商人员入厂前由HSE管理部实施一级HSE培训，进入各装置区域作业前由运行部实施二级HSE培训，培训结束经考试合格，作业前进行安全交底后方可作业。各运行部门应做好培训记录。 | 前期入场承包商培训记录完好
|  |  | 5.10.6.2 Visitors shall handle entry permits only when they have received entry training. 访客经入厂培训后方可办理入厂通行证。 | 后续涉及将按要求执行
|  | 5.10.6 HSE training for contractors and visitors 承包商及访客HSE 培训 | 5.10.6.3 Before the contractor and visitors enter the company, the reception department shall submit the corresponding safety training process from OA, and carry out the on-site training after receiving the approval. The contractor safety training should be applied for three days in advance, and the accurate information of the contractor personnel should be attached. 承包商及访客进入公司前，接待部门需从OA提交相应的安全培训流程，经批复后开展入厂培训。其中承包商安全培训需提前三天申请，并附承包商人员准确信息。 | 后续涉及将按要求执行
| Identification and evaluation of environmental factors 环境因素识别与评价 | 5.2.2.2 All relevant departments shall organize the personnel to identify the environmental factors that can be controlled or are expected to be exerted influence on from their activities, products and services, and to fill out the Form for Identification and Evaluation of Environ-mental Factors and feed it back to the HSE Dept. 各相关部门组织人员从其活动、产品、服务中识别出能够控制或可望施加影响的环境因素，填写《环境因素识别和评价表》并反馈到HSE管理部。 | Ask the department staff on the spot whether they are clear about the concept and identification of environmental factors, etc. 现场询问部门人员是否清楚环境因素概念及识别等 | 提问员工回答良好
|  | 5.2.7 Update of environmental factors 环境因素的更新 In case of any major change on the Company’s activities, products and services or any up-date of regulations and other requirements, all departments shall timely supplement and identify environmental factors and report to the HSE Dept. for evaluation of environmental factors to redefine the major environmental factors and conduct management on them. 当公司的活动、产品、服务发生较大变化或法规及其他要求更新时，各部门应及时对环境因素进行补充识别，并报HSE管理部进行环境因素评价，以重新确定重要环境因素并对其进行管理。 | Whether to carry out the environmental factor identification and evaluation work of the department in the current year, and whether to update the environmental factor identification and evaluation table and the list of major environmental factors in a timely manner 是否开展本部门当年度的环境因素识别和评价工作，是否及时更新环境因素识别和评价表和重要环境因素清单 | 环境因素识别已完成并上交
|  |  | Check whether the site is implemented according to the department's environmental factor list and the measures formulated 对照部门环境因素清单及制定的措施检查现场是否落实 | 已按要求落实
|  | 5.9.1.1 A comprehensive identification of environmental factors shall be carried out for device startup and shutdown as well as maintenance. 装置开、停工、检修应进行全面的环境因素识别。 | 1. Whether environmental factors are identified during the start-up, shutdown and maintenance of the device, and corresponding control measures are formulated. 2. Whether various control measures are implemented as required. 1.是否对装置开、停工及检修过程进行环境因素识别，并制定相应控制措施。 2.是否按要求落实各项控制措施。 | 已按要求做好识别
| Wastewater management 废水管理 | 5.3.1.1 All kinds of waste water must be tested to satisfied department control limit indicators formulated by the Company before discharge. 各类废水须经检测达到公司制定的分级控制指标后方可排放。 | 1. Whether the test is carried out in accordance with the annual environmental monitoring plan. 2. Check LIMS to see whether the discharge is carried out after the test results of the graded control indicators meet the standards, and whether the discharge does not meet the standards and whether to apply for abnormal discharge. 1.是否按照年度环境监测计划进行检测。 2.查LIMS，分级控制指标检测结果是否达标后排放，不达标外排是否申请异常排污。 | 含油污水化验分析登记正常。
|  | 5.3.1.6 Water Body Pollution Emergency Plan and Oil Spill Response Plan shall be prepared. 应当编制水体污染与溢油应急预案。 | 1. Whether the responsible units of each sewage outlet have formulated a plan to prevent water pollution and conduct regular drills. 2. Whether the Port and Reserve Department has prepared an oil spill emergency plan and conducted regular drills. 1.各污水外排口责任单位是否制定防水体污染预案，并定期演练。 2.港储部是否编制溢油应急预案，并定期演练。 | 已制定防污水污染预案
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 2）The operation department.: the drainage management system of the unit; the operation specifications and internal control process indicators; the diagram of drainage pipe network of the department (including: the layout of discharge point, discharge direction, the identifi-cation of sampling port, the pipe network for diverting wastewater from clean water, etc.) ; establish the waste water management ledger, etc. 运行部：本单位排水管理制度；操作规程、内控工艺指标；本部门排水管网图（应包括：排放点布置、排放去向、采样口标识、清污分流管网等）建立废水管理台帐等。 | 查资料： 1. Sewage discharge management system 污水排放管理制度 2. Drainage network diagram 排水管网图 3. Internal control process indicators 内控工艺指标（仅限在线分析仪表） 4. Wastewater management ledger 废水管理台账 | 三废管理细则已放置于外操室，员工清楚内容
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （3）Sewage treatment plants, sour water stripping units, etc. shall be in strict compliance with the operation specifications to ensure the up-to-standard discharge. 污水处理场、酸性水汽提等装置应严格遵守操作规程，确保达标排放。 | 1. Spot check whether the key operations of sewage treatment plants and acid water stripping devices have formulated operating procedures. 2. Spot check and verify whether the operations and indicator controls of each position of the team are carried out in accordance with the operating procedures. 1.抽查污水处理场、酸性水汽提装置的关键操作是否制定操作规程。 2.抽查、验证班组各岗位操作及指标控制是否按操作规程执行。 | 已按要求执行
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （5）All departments shall ensure that the drainage process is complete and in compliance with the requirements. It is forbidden to change the direction of pollution discharge without permission, and the drainage process may not be altered at will without approval. 各部门应确保排水工艺完整与符合要求，杜绝私自改变排污去向，未经批准不得随意变更排水工艺。 | Check whether the change in drainage process is carried out in accordance with the change management requirements and check the relevant change information. 变更排水工艺是否按变更管理要求执行，查相关变更资料。 | 暂无此方面变更
|  | 5.3.2.1 （20）Where the high-concentration waste water (such as the highly sulfur-containing, am-monia-containing, phenol-containing, acid-base sewage, etc.) needs to be discharged, the water volume and water quality shall be reported to the Scheduling & Dispatch Dept. and HSE Dept. and the downstream processing plant shall be contacted and given explanation about the situation at the same time to avoid impact on the sewage treatment plant. 高浓度废水（如高含硫、含氨、含酚、酸碱等污水）需排放时，应向计划调度部、HSE管理部报告水量、水质情况，同时与下游处理装置联系、说明情况，避免冲击污水处理场。 | Check the discharge of overlimt wastewater, and check the OA process of discharge. 检查超标废水产生情况，检查超标废水排放OA流程。 | 无废水超标情况
|  | 5.3.2.1 （21）All water discharged to the external environment must be analyzed to prove qualified before being discharged outwards. 所有排往外环境的水须经分析合格后方可外排。 | 1. Whether the water discharged to the external environment is sampled and analyzed according to the environmental monitoring plan. 2. Whether the monitoring items and monitoring frequency are implemented as required. 3. Whether abnormal analysis results are reported immediately and the causes of abnormalities are analyzed. 1.排往外环境的水是否按环境监测计划取样分析。 2.监测项目和监测频次是否按要求执行。 3.分析结果异常是否立即报告，并对异常原因进行分析。 | 无异常
|  | 5.3.3.6 The comparison between online monitoring data and manual monitoring data shall be conducted no less than once every quarter for the water quality online monitoring system. No unit or individual may dismantle, idle or alter the automatic monitoring equipment for pollution source. 水质在线监控系统每个季度应开展不少于1次的在线监测数据与人工监测数据的比对。任何单位和个人不得擅自拆除、闲置、改动污染源自动监测设备。 | 1. Whether the online monitoring data of the water quality online monitoring system is compared with the manual monitoring data every quarter, and check the comparison report or record. 2. Check the maintenance record of the water quality online monitoring system to see whether the calibration and maintenance are completed as required. 3. Check the integrity of the automatic monitoring equipment for sewage water quality and whether it has been dismantled, idled or modified. 1.每季度是否对水质在线监控系统开展在线监测数据与人工监测数据比对，查比对报告或记录。 2.查水质在线监控系统维护记录，是否按要求完成校验、维护。 3.查污水水质自动监测设备完好性，是否被拆除、闲置或改动。 | 已按要求登记
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.1 Regularly inspect the FGS system, evaluate the operating status of the system,record key parameters, compare historical data, and analyze the stability and performance of the system.定期对 FGS 系统进行检查，评估系统的运行状态，记录关键参数，对比历史数据，分析系统的稳定性和性能 5.3.3.2 Regular software updates and virus scans to ensure system security 定期进行软件更新和病毒扫描，确保系统安全性 | Whether the FGS system is checked regularly to ensure stable system performance, whether the software is updated and virus scanned regularly to ensure system security, and whether relevant records are complete. 是否定期对FGS系统进行检查，确保系统性能稳定，定期对软件进行更新和病毒扫描，确保系统安全性，相关记录是否齐全。 | 记录齐全
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.3 Clean the dust on the surface of the equipment in time to ensure good heat dissipation of the equipment; check the integrity of the power cord and connecting cables to prevent failuredue to aging or damage 及时清理设备表面灰尘，确保设备散热良好；检查电源线和连接电缆的完好性，防止因老化或破损导致故障 | Check and maintain the equipment to ensure the integrity of system components and check whether maintenance records are complete. 是否对设备进行检查和保养，确保系统部件性能完整，检查保养记录是否齐全 | FGS未出现故障
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.4 When a system failure occurs, the possible cause of the failure is determined based on the failure phenomenon, and corresponding troubleshooting measures are taken promptly to ensure the stable operation of the system. 当系统出现故障时，根据故障现象判断可能的故障原因，及时采取相应的故障排除措施，保障系 统的稳定运行。 5.3.3.5 Regularly conduct comprehensive calibration and debugging of the system to ensure the accuracy of various parameters and eliminate errors caused by long-term operation 定期对系统进行全面校准和调试，确保各项参数准确，消除因长期运行导致的误差。 | Whether the fault is promptly eliminated when it occurs, whether the system is fully calibrated and debugged regularly to ensure that all parameters are accurate, and whether the maintenance records are complete; 是否在出现故障时，及时排除故障，是否定期对系统进行全面校准和调试，确保各项参数准确，维修记录是否齐全； | FGS未出现故障
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.6 Establish and improve system maintenance work records, including inspection content, fault diagnosis, component replacement and other information, and organize and archive them to facilitate subsequent inquiries and analysis. 建立健全系统维修保养工作记录，包括检查内容、故障诊断、部件更换等信息，并整理归档，便于后续查询和分析。 | Whether a sound maintenance record has been established and whether the record content is complete; whether monthly work suggestions are made for the system operation. 是否建立健全维修保养记录，记录内容是否完整；是否对系统运行情况提出月度工作建议。 | 记录完整
| 5.5 Fire prevention inspections and hidden danger management 消气防监督检查和隐患治理 | 5.5.2 Rectification of hidden dangers 隐患整改 For the hidden dangers spotted during the fire inspection, the department concerned shall contact corresponding department and personnel for to tackle with them. Rectification of ordinary hidden dangers shall be performed by professionals organized by each department. Major hidden dangers shall be rectified after the discussion by HSE management committee, before which safety protection measures shall be implemented by the personnel of relevant departments. 对于防火检查中发现的隐患，由所在部门联系相关部门和人员进行处理。一般隐患由各部门组织专业人员进行整改；重大隐患经公司HSE管理委员会讨论后落实整改，整改前由有关部门人员落实安全防护措施。 | Whether hidden dangers found during fire prevention inspections have been rectified in a timely manner; whether problems that have not been rectified in a timely manner and major hidden dangers have been included in the hidden danger ledger and reported to the HSE Management Department in a timely manner. 防火检查中发现的隐患，是否及时落实整改；未及时落实整改的问题及重大隐患是否列入隐患台账，并及时上报HSE管理部。 | 已全部签字
|  |  |  | 加氢润滑油站内灭火器 XM11755 压力表面模糊 |  | 扣1分 |  | 加氢二班 |  | Wafi
|  |  |  | 11月8日二级火票气体分析日期填写错误。 |  | 扣2分 |  | 加裂三班 |  | 江志宁
|  |  |  | 加裂2号四合一故障，班组没及时检查反馈维护不到位 |  | 扣2分 |  | 加裂四班 |  | 江志宁
|  |  |  | 11月10二级火票监护人更换没做气体分析 |  | 扣2分 |  | 加裂一班 |  | 江志宁

## 日检表 (12)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分测量技改管线长度
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 11月10日，P103作业完成并拆除临时用电后，临时用电作业票未及时关闭。 |  | 扣2分 |  | 加裂一班 |  | Wafi
|  |  |  | 11月10日，下午作业恢复前未重新进行取样分析。 |  | 扣2分 |  | 加裂一班 |  | Wafi
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽考黄泽，卡尤木和麻力克回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 气分E303地面北侧服务站缺少两个胶垫，但是只有一个备用胶垫 |  | 扣2分 |  | 加裂三班 |  | 毛奕清
|  |  |  | 柴油加氢PRA管廊，航煤原料管排附近XM11025一个灭火器压力表面模糊。 |  | 扣1分 |  | 加氢三班 |  | 毛奕清

## 日检表 (11)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 今天无高风险作业
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 无
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽考张其拉，法尔汉回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 含油污水排水口未被沙袋有效封堵。 |  | 扣2分 |  | 加裂三班 |  | Wafi
|  |  |  | 服务站蒸汽胶皮管未安装，且接头缺失 |  | 扣2分 |  | 加裂三班 |  | Wafi
|  |  |  | 夜班整理五个垃圾箱 |  | 加3分 |  | 加裂二班 |  | 毛奕清

## 日检表 (10)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分技改线打压, 技改线搭脚手架和E101拆脚手架和加氢脚手架作业。
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽考李桂能，翟小杰，瑞祖安回答良好，肖斌，阿扎姆未答出 |  | 各扣2分 |  | 加裂一班 | 肖斌 阿扎姆 | 毛奕清
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 气分分析小屋旁胶皮管未盘整齐，远处有一根未使用的胶皮管，水线已连接但未使用。 |  | 扣2分 |  | 加裂一班 |  | 毛奕清
|  |  |  | 加裂小库房西侧服务站少一根胶皮管 |  | 扣2分 |  | 加裂一班 |  | 毛奕清
|  |  |  | 柴油加氢D502附近砂袋破损 |  | 扣2分 |  | 加氢一班 |  | 毛奕清
|  |  |  | 加裂二班，加裂三班志愿消防队签字表没按时签完 |  | 各扣2分 |  | 加裂二班加裂三班 |  | 江志宁
|  |  |  | 气分作业现场灭火器箱盖上放满工具， 加裂P103附近灭火器XM11475箱盖上全是黄油 |  | 扣2分 |  | 加裂一班 |  | 江志宁
|  |  |  | 加裂外操室垃圾桶里很新的手套随意丢弃 |  | 扣2分 |  | 加裂三班 |  | 江志宁
|  |  |  | 应急用空呼气瓶压力＜25 MPa。 |  | 扣2分 |  | 加氢三班 |  | Wafi
|  |  |  | 气防柜拉警戒线缺失2条，上夜班次交接不到位 |  | 扣2分 |  | 加氢三班 |  | Wafi

## 日检表 (7)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分循环水管线施工。 烟气检测已结束。
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 正常
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 今天抽考白鹤回答良好，安华回答错误。 |  | 扣2分 |  | 加氢四班 | 安华 | 毛奕清
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 劳动防护用品发放记录未签字 |  | 扣2分 |  | 加氢一班 | 郑棚 | Wafi
|  |  |  | 含油污水送水有记录，10月14日气分20：00分析记录未写，10月23日已翻倍考核，加裂14日已补上记录，气分的未补上。10月30日再次列入翻倍考核 |  | 扣4分 |  | 加裂一班 |  | 毛奕清
|  |  |  | 9月 任善华 HSE活动记录本未记录 |  | 扣2分 |  | 加裂一班 |  | 毛奕清
|  |  |  | 气分循环水线施工。抽考监护人回答多处错误 |  | 扣2分 |  | 加裂四班 | 袁茂波 | 毛奕清
|  |  |  | 配合更换空呼气瓶 |  | 加4分 |  | 加氢四班 | 陈盈嬟 | Wafi

## 周检表 (6)
HSE Weekly Checklist for No.2 Refining Department 炼油二部HSE周检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
| Safety Management System 安全管理制度 5.3 HSE hidden danger identification HSE 隐患排查 | 5.3.3.6 All departments shall prepare hidden danger identification form based on their discipline characteristics and actual production conditions and continue to improve such form in practice. 各部门应根据专业特点和实际生产情况制定隐患排查表，并在实际应用中不断持续改进。 5.3.4.1 Control requirements 治理要求 （1）For general hidden danger, departments involved shall immediately organize rectification. 对于一般隐患，由属地所在部门立即组织整改。 （2）For any general hidden danger which can’t be rectified immediately, the department involved shall develop a risk precaution plan and rectification plan, and rectify such danger within a specified timeframe. 对于暂不能整改的一般隐患，由属地部门制定风险防范措施和整改计划，限期整改。 5.3.6.1 All departments shall establish Hidden Danger Identification & Control Account. 各部门应建立《隐患排查治理台账》。 5.3.6.2 The hidden danger treatment should be recorded according to the "HSE Hidden Danger Investigation and Management Ledger" to achieve closed-loop rectification. 隐患治理情况应按《HSE 隐患排查治理台账》进行记录，做到闭环整改。 | Does the hidden danger investigation table meet the investigation requirements 隐患排查表是否满足排查要求 | 加氢隐患登记16个，加裂隐患登记22个，其中加裂巡检包维修隐患取消
|  |  | Whether the hidden danger investigation and management record is updated in time 隐患排查治理台账是否及时更新 | 已更新至最新版本
|  |  | Whether all staff are trained on hidden danger management 是否组织全员培训隐患治理情况 | 列入每月副班培训中
|  |  | Is the rectification carried out as planned 是否按计划整改 | 有条件的将立即整改
柴油D104PSV12301A/B，D202PSV21601A/B安全阀切出校验工作, 气分循环水线施工
手机及上岗证已按要求上墙
| Safety Management System 安全管理制度 5.4 Management of hazardous chemicals 危险化学品管理 | 5.4.2.2 The HSE management department shall supervise the establishment of hazardous chemicals ledger by all departments.. HSE 管理部监督各部门建立危险化学品台帐。 5.4.2.4 Each operation department must carry out targeted training on the knowledge of hazardous chemicals according to the hazardous chemicals involved in its own department,and staff shall be familiar with information on safety technology of hazardous chemical involved in the post to ensure stable operation and personal safety in production, storage, use, transportation and disposal of hazardous chemicals. 各运行部必须根据本部门涉及的危险化学品开展针对性的危险化学品知识培训，建立本部门《化学品普查表》与《危险化学品台帐》。员工应熟悉本岗位涉及的危化品安全技术信息，以保证危险化学品生产、储存、使用、运输、废弃处置等环节的平稳操作和人身安全。 5.4.2.5 Before using hazardous chemicals, the staff must know and grasp relevant MSDS andsafe operation instructions of hazardous chemicals, take relevant precautionary measures and prevent personal injuries. 员工使用危险化学品时，必须了解和掌握相应危险化学品安全技术说明书和安全操作规程有关内容，并采取相应的防范措施，避免发生人身伤害事故。 | Does the department have a hazardous chemicals register 部门是否建立危险化学品台账 | 已更新至最新版本（二部危化品台账）
|  |  | Whether to organize full-staff learning 是否组织全员学习 | 已放在外操室电脑供学习
| Safety Management System 安全管理制度 5.14.Hydrogen sulfide prevention 防硫化氢中毒安全管理 | 5.14.1 All departments shall set up eye-catching warning signs in both Chinese and English in places where hydrogen sulfide leakage may occur, and hydrogen sulfide warning signs shall be set up in eye-catching places in workplaces where hydrogen sulfide exists. A wind vane shall be set in the eye-catching position of the unit. 各部门在可能发生硫化氢泄漏的场所设置醒目的中英文警示标识，存在硫化氢的工作场所应在醒目位置设置硫化氢告知牌。装置醒目位置应设置风向标。 5.14.2 All personnel having access to hydrogen sulfide hazard area shall carry portablehydrogen sulfide alarms and protection devices as required. 所有进入可能存在硫化氢等有毒有害气体区域的巡检或作业的人员，必须佩戴相应的便携式气体检测仪和防护器具。集中作业时，作业小组应至少佩戴 1 台便携式气体检测仪。 5.14.3 The site concentration should be monitored at any time when the acid water, gas escape site, drain port, sampling port, storage tank metering port and other hidden parts are active. 在酸性水、瓦斯逸出部位、排液口、采样口、储罐计量口等隐患部位活动时，应随时监控现场浓度。 5.14.4 When entering hydrogen sulfide hazard area for patrol, operators shall conduct individual protection well and carry portable hydrogen sulfide alarm. In case of operation in hydrogen sulfide hazard area, it shall wear isolated respirator, set up warning signs around operation points and assign special personnel for monitoring. 员工在涉及接触硫化氢等有毒有害气体作业时，应做好个体防护，佩戴便携式气体检测仪和适宜呼吸防护用品，并有专人进行监护。 5.14.5 According to the working environment of different posts, all departments shall equip the operators with appropriate protective equipment. When the concentration of hydrogen sulfide is less than 50mg/m3, filter type anti-gas appliances can be used; When the hydrogen sulfide concentration is greater than 50mg/m3 or in the area where the medium leakage occurs and the concentration is unknown, isolated respiratory protective equipment should be used,and the gas supply device of the protective equipment should be placed on the upwind side. 各部门根据不同岗位的工作环境为作业人员配备适量适用的防护器材。当硫化氢浓度低于50mg/m3 时，可以使用过滤式防毒用具；当硫化氢浓度大于 50mg/m3 或在发生介质泄漏、浓度不明的区域内应使用隔离式呼吸防护用具，防护用具的供气装置应置于上风侧。 5.14.6 It is forbidden for any person to enter the area where hydrogen sulfide poisoning may occur without proper protective equipment, and it is forbidden to take off the protective equipment in the toxic area. 禁止任何人员不佩戴合适的防护器具进入可能发生硫化氢中毒的区域，禁止在有毒区内脱卸防毒用具。 5.14.7 When the hydrogen sulfide detection instrument alarms, the panel operator should remind the site personnel in time, the operator should wear protective equipment, check the leak point, prepare protective equipment and report to the superior, and evacuate the downwind personnel, prohibit all fire operations, quickly identify the cause of the leak and control the leak. 硫化氢检测仪器报警时，内操应及时提醒现场人员，作业人员应佩戴防护用具、检查泄漏点、准备防护用具并向上级报告，同时疏散下风向人员，禁止一切动火作业，迅速查明泄漏原因并控制泄漏。 5.14.8 Operation in hazardous places that may contain hydrogen sulfide, such as sewage wells and closed containers, shall be carried out in strict accordance with the management requirements of restricted Spaces of this system. 进入污水井、密闭容器等可能含硫化氢的危险场所作业，要严格按照本制度受限空间的管理要求执行。 5.14.9 When construction and maintenance personnel of contractors enter hydrogen sulfide hazard area to work, operation departments where they belong to shall organize construction contractors to conduct risk identification and notification of hydrogen sulfide hazards in operation area, and provide necessary protective devices and emergency rescue facilities. 承包商作业人员在涉及硫化氢等有毒有害气体环境中作业时，属地部门应对承包商作业人员进行硫化氢等有毒有害气体防中毒防窒息安全培训和安全交底，为其提供必要的呼吸防护器具和应急救护设施如正压式呼吸器，长管呼吸器等。 5.14.10 Any operator which is likely to come in contact with poisonous and harmful gases such as the hydrogen sulfide shall take trainings on poisoning and suffocation prevention and shall only take the job after being tested to be qualified. 凡可能接触硫化氢等有毒有害气体的操作人员，应接受防中毒、防窒息安全教育，经考核合格，方可上岗操作。 5.14.11 Departments that may have hydrogen sulfide leakage shall formulate emergency rescue plans and establish a first aid network, ensure that on-site first aid, evacuation and escort, and transport rescue channels are unblocked, conduct regular drills on emergency plans, and revise and improve them in time. 可能存在硫化氢泄漏的部门要制定应急救援预案并建立急救网络，保证现场急救、撤离护送、转运抢救通道畅通，对应急预案定期进行演练，并及时进行修订完善。 | Have employees been trained to prevent hydrogen sulfide poisoning 是否对员工进行防硫化氢中毒培训 | 已全员考试验收
Comprehensive Management 综合管理 | 5.2 HSE organization HSE 组织机构 | 5.2.2 Each department shall establish a safety management organization and establish the corresponding HSE Organization Ledger 各部门应建立安全管理组织机构，并建立相应的《HSE组织台帐》 | Whether the Organizational Ledger has been established and updated in a timely manner 是否建立了组织机构台帐，是否及时进行了更新 | 组织机构台账已建立，更新及时.
| 5.3 HSE policies and objectives HSE方针 | People-oriented, compliance with laws and regulations, community harmony, environmentfriendly, risk controllable. 以人为本、依法合规、社区和谐、环境友好、风险可控。 | Are employees clear about the company's policies, goals and commitments? 员工是否清楚公司方针目标与承诺 | 提问员工回答良好
| 5.4 HSE commitment HSE承诺 | 5.4.1 Abide by Brunei's laws and regulations, respect local customs and habits, and maintain a consistent attitude towards HSE in all business areas. 遵守文莱法律、法规，尊重当地风俗习惯，在所有业务领域对HSE的态度始终如一。 5.4.2 Care for life and health, protect the ecological environment, always adhere to zero tolerance for violations, and pursue the goal of zero injury, zero pollution, and zero accidents. 关爱生命健康，保护生态环境，始终坚持违章零容忍，追求零伤害、零污染、零事故的目标。 5.4.3 In order to ensure the achieve the goal, provide human, material and financial resources to support. 为保证目标的实现，提供人力、物力和财力等资源支持。 5.4.4 Regularly report HSE performance to the Brunei government, account for the needs of stakeholders such as investors, customers, and contractors, and actively accept supervision from all parties around us to achieve continuous improvement. 定期向文莱政府公布HSE业绩，关注投资者、客户、承包商等利益相关方需求，主动接受社会各界监督，实现持续改进。 | Are employees clear about the company's policies, goals and commitments? 员工是否清楚公司方针目标与承诺 | 今天抽查郭天英，徐红建，刘俊隆回答良好。刘磊未答出
| 5.9 HSE meeting HSE 会议 | 5.9.2.3 Each department holds a regular HSE meeting once a week. 各部门 HSE 例会每周召开一次。 5.9.3.3 HSE regular meeting of each department 各部门 HSE 例会 （1） Communicate the requirements of HSE meetings at all levels of the company and the recent safety production situation of the company. 传达公司各级 HSE 例会的要求及近期公司安全生产形势。 （2） Arrange HSE work of the department, and solve HSE related problems in the work of each team and staff. 布置本部门 HSE 工作，解决各班组及员工工作中 HSE 相关问题。 | The content of the company's HSE regular meeting was carefully communicated. The HSE regular meeting of this department was held on time. 公司HSE例会内容认真传达 本部门HSE例会按时召开 | 公司例会内容交接班时进行宣贯，并将例会纪要发到群里；部门例会每月末按时召开
| 5.14 HSE assessment HSE考核 | 5.14.2 Each department shall refer to the Company's "Performance Appraisal Measures" or refine the performance appraisal system of its own department to assess, reward and punish the HSE work of its own department, and establish the HSE assessment reward and punishment ledger. 各部门引用公司《绩效考核办法》或细化为本部门绩效考核制度，对本部门的HSE工作情况进行考核奖惩，并建立 HSE 考核奖惩台帐。 | Department’s HSE assessment status 部门的HSE考核情况 | 已在日周月检表内体现
Comprehensive Management 综合管理 | 5.16 Accident and incident management 事故事件管理 | 5.16.4.1 Each operation department shall encourage its employees to report near-miss accidents, and organize investigations and analyses on the near-miss accidents to find out the root cause and prevent the reoccurrence of the accidents. 各运行部门应鼓励并奖励员工报告未遂事件，并组织对未遂事件进行调查、分析，找出事故根 源，预防事故发生。 | Did the department make any request on reporting nearmiss incident? 部门是否对未遂事件进行过要求 | 本周没有未遂事件
|  | 5.16.5.1 incident and accident management requirements 事故、 事件报告要求 After an operation department accident or incident occurs, the occurrence department shall immediately report to the dispatch room, the person in charge of the department and the HSE Management Department, and submit a Preliminary Report Form of Accident (Incident) to the HSE Department via email within 24 hours. 发生事件、运行部级事故后，发生部门应立即报告调度室、本部门负责人和 HSE 管理部， 24 小时内通过邮箱向 HSE 管理部提报《事故（事件） 初步报告表》。 | Whether departmental accidents have been reported as required 部门事故事件是否按要求进行了报告 | 本周无事故事件发生
|  | 5.16.6.1 Incident investigation 事件调查 Where the incident submitted to the "Accident (incident) Preliminary Report Form", the occurrence department shall organize the incident investigation within one week after the occurrence of the incident, prepare the incident investigation record form, and the department shall file the record. 凡提报《事故（事件）初步报告表》的事件，发生部门应在事件发生后一周内组织事件调查，编写《事故（事件） 报告表》 ， 报 HSE 管理部。 | Whether the department's accident incidents are investigated as required 部门事故事件是否按要求开展调查 | 本周无事故事件发生
|  |  | 事故事件台帐已经建立，台帐内容填写不全，维护不及时。 | 事故事件台账已完善
|  | 5.16.7.1 In the course of handling of accidents and incidents, the principles of “Four do not let go”, namely, not allowing any existence of unclear accident causes, not allowing any missing of punishment on accountable parties of the accident, not allowing any failure in implementing the rectification measures and not allowing any failure in mass education targeting relevant liable personnel. 事故、事件处理都要坚持“四不放过”原则，即事故原因未查清不放过、责任人员未处理不放过、整改措施未落实不放过、有关人员未受到教育不放过。 | For accidents in the department, has the department adhered to the "Four Do No-Let-Go" principle? For accidents in other departments of the company, has the department organized employees to learn? 对于部门的事故，部门是否坚持了四不放过原则，对于公司其他部门的事故，是否组织了本部门员工进行学习 | 本周无事故事件发生
|  | 5.5.2.3 Issuance of protection supplies 防护用品发放 （1）The operation department must, according to the requirements of work safety and prevention of occupational hazards, issue to employees PPE with different protection functions and record the issuance of PPE according to “One Person One Record” (See HYBN-T7-08-4001-2024-3 Template of PPE Issuing Records); 运行部门必须根据安全生产和防止职业性危害的需要，发给员工具有不同防护功能的劳动防护用品并按照“一人一卡” 做好劳动防护用品发放记录（参照HYBN-T7-08-4001-2024-3劳动防护用品发放记录模板）; | Whether to establish an employee PPE distribution ledger, whether the ledger is true and complete. 是否建立员工PPE发放台账，台账是否真实、完整。 | 台账已按要求建立，检查没问题
|  |  | XXX部有劳保发放记录但未建立“一人一卡。要求部门按照“一人一卡”劳保发放记录落实。 | 按照一人一卡落实
|  | 5.6.3.1 Operation protection 作业防护 （1）Prior to operation, workplaces where toxic gases may be present shall be tested for toxic gas concentration; 作业前对可能存在有毒气体的工作场所进行有毒气体浓度检测； | Do employees know which toxic and hazardous gases are present in their department and the required protective equipment? 员工是否知道部门有哪一些有毒有害气体？是否懂需要用什么劳动防护用品？ Does management have a list of hazardous substances/MSDS list? Has it been shared to employees? Do employee know how to read/obtain information from a MSDS? 管理人员是否建立部门内部的有毒有害气体清单并做好内部宣贯？员工是否了解MSDS内容？ Does employee know what does IDLH means? 员工是否知道IDLH指什么？IDLH是英文Immediately Dangerous to Life or Health concentration的缩写，指的是直接致害浓度。 | 提问任善华，玛莎蒂娜，张磊磊，刘宝军，阿菲，刘亮，刘亚军回答良好，李桂能，翟小杰，肖斌，瑞祖安，阿扎姆未答出。 |  | 各扣2分 |  | 加氢一班加裂一班 |  | 毛奕清
|  | 5.6.1.4 Employees who participate in poisonous and harmful operations must undergo occupational health education beforehand, keep records of Occupational Health training records (See HYBN-T7-08-4003-2024-1 Occupational Health Training Records) and be provided with effective PPE. 对参加有毒有害作业员工，必须事先进行职业健康教育，做好职业健康培训记录(见HYBN-T7-08-4003-2024-1职业健康培训档案) 并提供有效的劳动防护用品。 5.6.1.7 Occupational Health regular training materials should be recorded and accompanied with proper records (See HYBN-T7-08-4003-2024-1 Occupational Health Training Archives) and filed for storage. 职业健康专业定期学习材料应做好职业健康培训记录 (见HYBN-T7-08-4003-2024-1职业健康培训档案) 并做好存档。 | Check if training records have been established? 培训档案是否按照要求建立？ Check whether OH poster had been published and shared with employees on a timely basis and if records had been logged. 检查职业健康海报是否已及时发布并与员工分享，并查看是否有记录登记 | 本月健康简报已打印放置于外操室外墙上
|  | 5.6.2.1 Noise protection 噪声防护 （1）Employees must wear earplugs or earmuffs when they are exposed to workplaces with excessive noise (greater than 85 dB). 员工接触噪声超标 (大于85dB) 的作业场所，必须配戴防噪声耳塞或耳罩； | Are employees aware of noise exposure limits? 员工是否知道噪声超标指标？ If noise exposure exceeds limit, what should you do? 如果超标，是否知道要佩戴什么防护用品？ | 提问员工希达雅 ,萨吉和那比尔回答良好
|  | 5.6.2.2 Noise monitoring 噪声监测 （1）Conduct monitoring of noise at workplaces and noise exposure of employees semiannually; 每半年对作业场所噪声及员工噪声暴露情况至少进行一次监测； | Do employees know the internal noise monitoring points within their department? 员工是否知道部门内部噪声监测点在哪里？ | 提问员工希达雅 ,萨吉和那比尔回答良好
|  | 5.6.2.4 Hearing protection 听力保护 （1）According to local laws and regulations, employees at workplaces where there is excessive noise level of more than 85 db(A) should undergo annual audiometry testing to ascertain the impact of excessive noise exposure and to prevent long term hearing loss. 在噪音水平超过85dB(A)的工作场所工作的员工应接受年度听力测试，以确定过度噪音暴露的影响并防止长期听力损失。 | Are employees aware of the health effects of noise and the legal requirement for annual hearing tests? 员工是否知道噪声对健康的影响？是否知道法律法规要求一年做几次听力测试？ | 提问员工希达雅 ,萨吉和那比尔回答良好
|  | 5.6.6.2 When working with acids and bases, employees must wear acid and alkali resistant clothes and wear acid and alkali resistant gloves and glasses. Operation departments are responsible for maintaining the eye wash and emergency shower facilities on the production site. It is required to test the eyewash and emergency shower facilities once per week and to make regular inspection records (See HYBN-T7-08-4004-2024-1 Template of Eyewash and Emergency Shower Inspection Records). 接触酸碱操作时，岗位员工必须穿好防酸碱服，戴好防酸碱手套和眼镜。运行部门负责维护生产现场的洗眼器和水喷淋设施，要求至少每周一次对洗眼器和水喷淋设施进行测试，并做好定期检查记录工作 (见HYBN-T7-08-4004-2024-1洗眼器喷淋系统检查表)； | Check eyewash inspection records. 检查现场洗眼器工况及喷淋情况和部门检查记录。 Do employees know the monitoring frequency? 询问员工是否知道检查频次 | 提问员工回答良好
|  |  | 质检部洗眼器过滤网上积聚残留物，导致喷嘴堵塞。 | 洗眼器出水口通畅
|  | 5.6.7.1 Each operating department is responsible for the management of illumination in each workplace. Timely contact electrical department when lighting is insufficient. 每个运营部门负责管理每个工作场所的照明。照明不足时及时联系电气部门。 | Check illumination in each field operating room 检查外操室的照明 | 照明灯及手电筒完好备用
| Medical aid 医疗救护 | 5.8.1.1 First aiders will be provided with an individual identification card for easy recognition on site and in each work station. Site workers must display their first aider cards in the notice board on site, while for office workers, first aider cards must be displayed at designated notice boards. 急救人员将获得一张个人身份卡，以便在现场和每个工作站进行识别。现场员工的急救卡需在上 岗证公告栏展示，办公楼(含检维修楼、中控楼、集控楼等)需在制定公告栏展示。 | Check whether first aider card is displayed at designated notice board and if employee always bring their first aider card 检查急救员卡是否张贴在指定的公告板上，并确认员工是否随时携带急救员卡。 | 已贴在墙上
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （2）Inside each First Aid Kit shall be equipped with inspection form to list the necessary supplies and their quantities for easy inspection and replenishment. Refer to HYBN-T7-08-4005-2024-2 Template of First Aid Booklet. 每个急救箱内都要配备急救箱检查表，列出必备的用品及其数量，以方便检查和补充，详见HYBN-T7-08-4005-2024-2急救药箱记录表。 | Whether the list of supplies is paired according to the requirements and check for inspection records 急救药箱内容是否按要求配备并检查记录 | 已按要求做好检查
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （4）Oral medicines shall not be placed in the medical kit. 口服药不得放入药箱内。 | Whether the oral medicine is also in the first aid kit. 口服药是否也在急救药箱中 | 口服药不在药箱中
|  |  | 灵活焦化外操室有4包滤毒盒和6个半面罩已超过使用有效期。重整外操室(FAR3)急救药箱内存有口服药及过期医用手套。 | 药品全部在有效期内且放在药箱外，面罩合格
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （5）The position of the medical kit shall be clear and visible indoors and there shall be a position indicator. The medical kit must not be locked and should be easily accessible during work. 医药箱位置在室内清楚可见，有位置标识指示，医药箱不得上锁并在工作期间易于取用。 | Check whether first aid kit has proper signage and indicator, if first aid kit is accessible or not 检查急救箱是否有正确的标识和指示，并确认急救箱是否易于取用 | 状态正常
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （6）Operating departments shall appoint department first aiders to check the condition of the first aid kit, quality and validity of the medicines once per month. If the medicines are inadequate or expired, such persons shall timely report to the HSE Dept. to apply for procurement, replenishment and replacement in time. 运行部门指定部门急救人员每月对急救药箱情况、药物的质量、有效期进行检查，不足或过期时 应及时向 HSE 管理部申请购买，及时补充、更换。 | Whether the first aid kit is checked regularly by department first aiders, whether the use record and the check record are complete 药箱是否被部门急救人员定期进行检查，使用记录及检查记录是否完整 | 检查合格
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.1 Education training requirements 教育和培训要求 | 5.10.1.2 All departments shall be responsible for preparing and implementing their own annual HSE education and training plans and establishing HSE training records. 各部门负责编制和实施本部门HSE年度教育和培训计划、建立HSE教育培训档案与HSE培训台帐。 | 按年度计划进行培训并存档
|  |  | 5.10.1.3 Personnel who have not passed the HSE training and examination shall not be employed. The eligibility criteria are that the test score exceeds 80% of the total score on the paper. 未经HSE培训考核合格的人员不得上岗。合格标准为考试分数超过卷面总分的80%。 | 上岗员工的安全考试成绩均为80分以上
|  | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.1 New employees in operation positions shall receive 3 level HSE training, the time is 72 academic hours, and the annual refresher training time is not less than 20 academic hours, and they can only take the post after passing the examination. 生产操作岗位新员工应接受三级HSE培训，时间为72学时，每年再培训时间不少于20学时，并经考试合格后方可上岗。 | 已按要求落实
|  | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.3 Employees subject to occupation mobility or job transfer or leaving their posts for more than six months shall receive HSE training at levels of operation dept. and team. 员工在公司内工作调动、转岗以及脱离岗位六个月以上者，应进行运行部、班组级HSE培训，经考试合格后方可上岗。 | 已按要求执行
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.4 When the operation department adopts new processes, new technologies, new materials or uses new equipment, it shall conduct targeted safety training for the relevant employees. 运行部采用新工艺、新技术、新材料或者使用新设备时，应当对有关从业人员进行针对性的安全培训。 | 如有涉及将按要求执行
|  | 5.10.5 Team-based HSE activities 班组 HSE 活动 | 5.10.5.1 All departments shall conduct department-based and team-based HSE activities. 各部门应开展以部门、班组为单位的HSE活动。 | 本月副班培训已全部完成
|  |  | 5.10.5.2 Group HSE activities shall be studied intensively at least once a month, and the learning time shall not be less than 2 academic hours each time. The department's HSE activities shall be conducted once a month, with no less than 1 academic hour each time. 班组HSE活动每月集中学习不少于一次，每次学习时间不少于2学时。部门HSE活动每月1次，每次不少于1学时。 | 已按要求完成培训
|  |  | 5.10.5.3 HSE Management Department shall formulate HSE activity learning plan of team and group every quarter. On the basis of meeting the requirements of the company, each department may arrange the learning of production process safety management knowledge, emergency drills and other HSE related activities. HSE管理部每季度制定班组HSE活动学习计划。各部门在满足公司要求的基础上，可安排生产过程安全管理知识学习、应急演练及其他与HSE相关的活动。 | 按要求开展
|  | 5.10.5 Team-based HSE activities 班组 HSE 活动 | 5.10.5.4 HSE activities of the team shall be recorded in detail in the team HSE activity record, including personnel attendance, learning records, etc. 班组HSE活动情况应在班组HSE活动记录上详细记录，包括人员出勤、学习记录等内容。 | HSE活动记录本加氢加裂四个班本月未记录
|  |  | 抽查XXX班组《班组HSE活动学习记录》记录不规范，2024年12月12日班组记录，XXX未参加活动，未参加人员原因未填写。 | 班组活动记录本已全部完成记录
|  |  | 5.10.5.5 The department leader shall check the learning status of the team and sign the activity record book before the 10th of each month. The management personnel of HSE department shall conduct spot checks on HSE activities from time to time. 部门领导应对班组学习情况进行检查，并于每月10号前在活动记录本上签字，HSE部管理人员不定期对HSE活动情况进行抽查。 | 已按要求完成
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.6 HSE training for contractors and visitors 承包商及访客HSE 培训 | 5.10.6.1 Before contractor personnel enter the factory, the HSE Management Department will conduct Level I HSE training. Before entering the operation area of each unit, the Operation Department will conduct Level II HSE training. After the training, the contractors must pass the examination and conduct safety briefings before operation. Each operating department should keep training records. 承包商人员入厂前由HSE管理部实施一级HSE培训，进入各装置区域作业前由运行部实施二级HSE培训，培训结束经考试合格，作业前进行安全交底后方可作业。各运行部门应做好培训记录。 | 前期入场承包商培训记录完好
|  |  | 5.10.6.2 Visitors shall handle entry permits only when they have received entry training. 访客经入厂培训后方可办理入厂通行证。 | 后续涉及将按要求执行
|  | 5.10.6 HSE training for contractors and visitors 承包商及访客HSE 培训 | 5.10.6.3 Before the contractor and visitors enter the company, the reception department shall submit the corresponding safety training process from OA, and carry out the on-site training after receiving the approval. The contractor safety training should be applied for three days in advance, and the accurate information of the contractor personnel should be attached. 承包商及访客进入公司前，接待部门需从OA提交相应的安全培训流程，经批复后开展入厂培训。其中承包商安全培训需提前三天申请，并附承包商人员准确信息。 | 后续涉及将按要求执行
| Identification and evaluation of environmental factors 环境因素识别与评价 | 5.2.2.2 All relevant departments shall organize the personnel to identify the environmental factors that can be controlled or are expected to be exerted influence on from their activities, products and services, and to fill out the Form for Identification and Evaluation of Environ-mental Factors and feed it back to the HSE Dept. 各相关部门组织人员从其活动、产品、服务中识别出能够控制或可望施加影响的环境因素，填写《环境因素识别和评价表》并反馈到HSE管理部。 | Ask the department staff on the spot whether they are clear about the concept and identification of environmental factors, etc. 现场询问部门人员是否清楚环境因素概念及识别等 | 提问员工回答良好
|  | 5.2.7 Update of environmental factors 环境因素的更新 In case of any major change on the Company’s activities, products and services or any up-date of regulations and other requirements, all departments shall timely supplement and identify environmental factors and report to the HSE Dept. for evaluation of environmental factors to redefine the major environmental factors and conduct management on them. 当公司的活动、产品、服务发生较大变化或法规及其他要求更新时，各部门应及时对环境因素进行补充识别，并报HSE管理部进行环境因素评价，以重新确定重要环境因素并对其进行管理。 | Whether to carry out the environmental factor identification and evaluation work of the department in the current year, and whether to update the environmental factor identification and evaluation table and the list of major environmental factors in a timely manner 是否开展本部门当年度的环境因素识别和评价工作，是否及时更新环境因素识别和评价表和重要环境因素清单 | 环境因素识别已完成并上交
|  |  | Check whether the site is implemented according to the department's environmental factor list and the measures formulated 对照部门环境因素清单及制定的措施检查现场是否落实 | 已按要求落实
|  | 5.9.1.1 A comprehensive identification of environmental factors shall be carried out for device startup and shutdown as well as maintenance. 装置开、停工、检修应进行全面的环境因素识别。 | 1. Whether environmental factors are identified during the start-up, shutdown and maintenance of the device, and corresponding control measures are formulated. 2. Whether various control measures are implemented as required. 1.是否对装置开、停工及检修过程进行环境因素识别，并制定相应控制措施。 2.是否按要求落实各项控制措施。 | 已按要求做好识别
| Wastewater management 废水管理 | 5.3.1.1 All kinds of waste water must be tested to satisfied department control limit indicators formulated by the Company before discharge. 各类废水须经检测达到公司制定的分级控制指标后方可排放。 | 1. Whether the test is carried out in accordance with the annual environmental monitoring plan. 2. Check LIMS to see whether the discharge is carried out after the test results of the graded control indicators meet the standards, and whether the discharge does not meet the standards and whether to apply for abnormal discharge. 1.是否按照年度环境监测计划进行检测。 2.查LIMS，分级控制指标检测结果是否达标后排放，不达标外排是否申请异常排污。 | 含油污水化验分析登记正常。
|  | 5.3.1.6 Water Body Pollution Emergency Plan and Oil Spill Response Plan shall be prepared. 应当编制水体污染与溢油应急预案。 | 1. Whether the responsible units of each sewage outlet have formulated a plan to prevent water pollution and conduct regular drills. 2. Whether the Port and Reserve Department has prepared an oil spill emergency plan and conducted regular drills. 1.各污水外排口责任单位是否制定防水体污染预案，并定期演练。 2.港储部是否编制溢油应急预案，并定期演练。 | 已制定防污水污染预案
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 2）The operation department.: the drainage management system of the unit; the operation specifications and internal control process indicators; the diagram of drainage pipe network of the department (including: the layout of discharge point, discharge direction, the identifi-cation of sampling port, the pipe network for diverting wastewater from clean water, etc.) ; establish the waste water management ledger, etc. 运行部：本单位排水管理制度；操作规程、内控工艺指标；本部门排水管网图（应包括：排放点布置、排放去向、采样口标识、清污分流管网等）建立废水管理台帐等。 | 查资料： 1. Sewage discharge management system 污水排放管理制度 2. Drainage network diagram 排水管网图 3. Internal control process indicators 内控工艺指标（仅限在线分析仪表） 4. Wastewater management ledger 废水管理台账 | 三废管理细则已放置于外操室，员工清楚内容
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （3）Sewage treatment plants, sour water stripping units, etc. shall be in strict compliance with the operation specifications to ensure the up-to-standard discharge. 污水处理场、酸性水汽提等装置应严格遵守操作规程，确保达标排放。 | 1. Spot check whether the key operations of sewage treatment plants and acid water stripping devices have formulated operating procedures. 2. Spot check and verify whether the operations and indicator controls of each position of the team are carried out in accordance with the operating procedures. 1.抽查污水处理场、酸性水汽提装置的关键操作是否制定操作规程。 2.抽查、验证班组各岗位操作及指标控制是否按操作规程执行。 | 已按要求执行
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （5）All departments shall ensure that the drainage process is complete and in compliance with the requirements. It is forbidden to change the direction of pollution discharge without permission, and the drainage process may not be altered at will without approval. 各部门应确保排水工艺完整与符合要求，杜绝私自改变排污去向，未经批准不得随意变更排水工艺。 | Check whether the change in drainage process is carried out in accordance with the change management requirements and check the relevant change information. 变更排水工艺是否按变更管理要求执行，查相关变更资料。 | 暂无此方面变更
|  | 5.3.2.1 （20）Where the high-concentration waste water (such as the highly sulfur-containing, am-monia-containing, phenol-containing, acid-base sewage, etc.) needs to be discharged, the water volume and water quality shall be reported to the Scheduling & Dispatch Dept. and HSE Dept. and the downstream processing plant shall be contacted and given explanation about the situation at the same time to avoid impact on the sewage treatment plant. 高浓度废水（如高含硫、含氨、含酚、酸碱等污水）需排放时，应向计划调度部、HSE管理部报告水量、水质情况，同时与下游处理装置联系、说明情况，避免冲击污水处理场。 | Check the discharge of overlimt wastewater, and check the OA process of discharge. 检查超标废水产生情况，检查超标废水排放OA流程。 | 无废水超标情况
|  | 5.3.2.1 （21）All water discharged to the external environment must be analyzed to prove qualified before being discharged outwards. 所有排往外环境的水须经分析合格后方可外排。 | 1. Whether the water discharged to the external environment is sampled and analyzed according to the environmental monitoring plan. 2. Whether the monitoring items and monitoring frequency are implemented as required. 3. Whether abnormal analysis results are reported immediately and the causes of abnormalities are analyzed. 1.排往外环境的水是否按环境监测计划取样分析。 2.监测项目和监测频次是否按要求执行。 3.分析结果异常是否立即报告，并对异常原因进行分析。 | 无异常
|  | 5.3.3.6 The comparison between online monitoring data and manual monitoring data shall be conducted no less than once every quarter for the water quality online monitoring system. No unit or individual may dismantle, idle or alter the automatic monitoring equipment for pollution source. 水质在线监控系统每个季度应开展不少于1次的在线监测数据与人工监测数据的比对。任何单位和个人不得擅自拆除、闲置、改动污染源自动监测设备。 | 1. Whether the online monitoring data of the water quality online monitoring system is compared with the manual monitoring data every quarter, and check the comparison report or record. 2. Check the maintenance record of the water quality online monitoring system to see whether the calibration and maintenance are completed as required. 3. Check the integrity of the automatic monitoring equipment for sewage water quality and whether it has been dismantled, idled or modified. 1.每季度是否对水质在线监控系统开展在线监测数据与人工监测数据比对，查比对报告或记录。 2.查水质在线监控系统维护记录，是否按要求完成校验、维护。 3.查污水水质自动监测设备完好性，是否被拆除、闲置或改动。 | 已按要求登记
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.1 Regularly inspect the FGS system, evaluate the operating status of the system,record key parameters, compare historical data, and analyze the stability and performance of the system.定期对 FGS 系统进行检查，评估系统的运行状态，记录关键参数，对比历史数据，分析系统的稳定性和性能 5.3.3.2 Regular software updates and virus scans to ensure system security 定期进行软件更新和病毒扫描，确保系统安全性 | Whether the FGS system is checked regularly to ensure stable system performance, whether the software is updated and virus scanned regularly to ensure system security, and whether relevant records are complete. 是否定期对FGS系统进行检查，确保系统性能稳定，定期对软件进行更新和病毒扫描，确保系统安全性，相关记录是否齐全。 | 记录齐全
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.3 Clean the dust on the surface of the equipment in time to ensure good heat dissipation of the equipment; check the integrity of the power cord and connecting cables to prevent failuredue to aging or damage 及时清理设备表面灰尘，确保设备散热良好；检查电源线和连接电缆的完好性，防止因老化或破损导致故障 | Check and maintain the equipment to ensure the integrity of system components and check whether maintenance records are complete. 是否对设备进行检查和保养，确保系统部件性能完整，检查保养记录是否齐全 | FGS未出现故障
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.4 When a system failure occurs, the possible cause of the failure is determined based on the failure phenomenon, and corresponding troubleshooting measures are taken promptly to ensure the stable operation of the system. 当系统出现故障时，根据故障现象判断可能的故障原因，及时采取相应的故障排除措施，保障系 统的稳定运行。 5.3.3.5 Regularly conduct comprehensive calibration and debugging of the system to ensure the accuracy of various parameters and eliminate errors caused by long-term operation 定期对系统进行全面校准和调试，确保各项参数准确，消除因长期运行导致的误差。 | Whether the fault is promptly eliminated when it occurs, whether the system is fully calibrated and debugged regularly to ensure that all parameters are accurate, and whether the maintenance records are complete; 是否在出现故障时，及时排除故障，是否定期对系统进行全面校准和调试，确保各项参数准确，维修记录是否齐全； | FGS未出现故障
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.6 Establish and improve system maintenance work records, including inspection content, fault diagnosis, component replacement and other information, and organize and archive them to facilitate subsequent inquiries and analysis. 建立健全系统维修保养工作记录，包括检查内容、故障诊断、部件更换等信息，并整理归档，便于后续查询和分析。 | Whether a sound maintenance record has been established and whether the record content is complete; whether monthly work suggestions are made for the system operation. 是否建立健全维修保养记录，记录内容是否完整；是否对系统运行情况提出月度工作建议。 | 记录完整
| 5.5 Fire prevention inspections and hidden danger management 消气防监督检查和隐患治理 | 5.5.2 Rectification of hidden dangers 隐患整改 For the hidden dangers spotted during the fire inspection, the department concerned shall contact corresponding department and personnel for to tackle with them. Rectification of ordinary hidden dangers shall be performed by professionals organized by each department. Major hidden dangers shall be rectified after the discussion by HSE management committee, before which safety protection measures shall be implemented by the personnel of relevant departments. 对于防火检查中发现的隐患，由所在部门联系相关部门和人员进行处理。一般隐患由各部门组织专业人员进行整改；重大隐患经公司HSE管理委员会讨论后落实整改，整改前由有关部门人员落实安全防护措施。 | Whether hidden dangers found during fire prevention inspections have been rectified in a timely manner; whether problems that have not been rectified in a timely manner and major hidden dangers have been included in the hidden danger ledger and reported to the HSE Management Department in a timely manner. 防火检查中发现的隐患，是否及时落实整改；未及时落实整改的问题及重大隐患是否列入隐患台账，并及时上报HSE管理部。 | 已全部签字
|  |  |  | 11月5日夜班未打扫公共区域卫生 |  | 扣2分 |  | 加裂三班 |  | Wafi
|  |  |  | 靠近1030-P205蒸汽胶皮管接头未用铁丝固定 |  | 扣2分 |  | 加氢一班 |  | Wafi

## 日检表 (5)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分循环水管线施工
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 2日特级火票随意涂改，JHA检修部监护人没签字。 |  | 扣2分 |  | 加裂一班 | 王杰 | 江志宁
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 抽查法扎娜竺暄栋，艾米里，希达雅，刘成伟，刘波，法扎娜，穆斯塔克姆，那比尔，于妃娜回答良好，贾兹力，罗庆通，法婷未答出， |  | 各扣2分 |  | 加氢二班加裂二班 |  | 毛奕清
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 柴油PRA管廊1020-E101东XM11106下半月已签名 |  | 扣1分 |  | 加氢二班 | 牛银泉 | 毛奕清

## 日检表 (4)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 气分循环水管线施工
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 气分循环水管线施工，有人进入施工区域进行与作业票内容不相符的工作。被公司检查发现 |  | 扣5分 |  | 加裂三班 | 黄泽 | 毛奕清
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 提问Sarah萨拉 和Liew Jun Lung 刘俊隆回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 加氢PRA管廊登高车请放指定位置 |  | 不扣分 | 11月5日前整改 | 加氢三班 |  | 毛奕清
|  |  |  | 加氢含油污水池旁XM11750箱子内有螺钉，上次已考核，本次翻倍考核 |  | 扣2分 |  | 加氢三班 | RAFI | 毛奕清
|  |  |  | 加裂未转化油去焦化采样，直蜡采样处地面明显油渍，请铺设吸油毡，附近旧吸油毡请更换。 |  | 扣2分 | 11月5日前整改 | 加裂三班 |  | 毛奕清
|  |  |  | 消防软管卷盘箱 SG11156、SG11157（K102C电机西南侧（二层））漏检 |  | 扣2分 |  | 加裂三班 |  | Wafi
|  |  |  | 灭火器 XM11529（P206B东北侧）压力表刻度模糊不可读。 |  | 扣1分 |  | 加裂一班 |  | Wafi
|  |  |  | 危废桶桶盖破损被风吹落，雨水进入桶内，当班未发现 |  | 扣2分 |  | 加氢三班 |  | Wafi

## 日检表 (3)
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 加裂P102流量计处拆脚手架, 气分循环水线动火
|  |  | 抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。 | 气分循环水线动火，作业人联未交到作业监护人手上，由于主动给他们了，他们未接收，考核减半。 |  | 扣1分 |  | 加裂四班 | 穆尼尔 | 毛奕清
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | IIs the department's four-in-one alarm device calibrated on time? 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
|  |  | 在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识 | 佩戴正常
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
手机和上岗证齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
|  |  | 2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。 | 分析及时记录，无不合格
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 加裂压缩机房附近发现未污染手套丢入危废桶，违反分类收集要求，属劳保浪费。当班未发现 |  | 扣2分 |  | 加裂四班 |  | Wafi
|  |  |  | 加氢含油污水泵附近发现干净抹布丢入危废桶，违反分类收集要求，属物资浪费。当班未发现 |  | 扣2分 |  | 加氢四班 |  | Wafi
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 提问焦涛，CHIN YIN YEE，祖柏达，沈伟回答良好
|  |  | 炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。 | 提问员工回答良好
|  |  | 检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。 | 提问员工回答良好
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
|  |  | 加氢SG 11020消防栓门把手损坏 | 所有受损的消防设施已完成整改，复查正常。
|  |  | 加裂文方员工对二氧化碳灭火器使用不熟悉 | 提问员工回答良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全； | 雨淋阀组巡查正常，记录到交接班日志
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 检查正常
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态
|  |  |  | 1040-A202D顶三层5处编号褪色严重，请使用油漆笔重新标记。 |  | 扣2分 | 11月5日前整改 | 加裂四班 |  | 毛奕清
|  |  |  | 协助整理放置防火布 |  | 加2分 |  | 加氢四班 |  | 毛奕清
|  |  |  | 1040-A202C旁有长期未使用的警戒带。请回收整理。 |  | 扣2分 |  | 加裂四班 |  | 毛奕清
|  |  |  | 1040-M202平台东侧XM11392内两个灭火器底部无除锈刷漆痕迹。 |  | 扣2分 |  | 加裂四班 |  | 毛奕清
|  |  |  | 《逃生面罩检查记录表》《气防柜检查记录表》均未签字 |  | 扣2分 |  | 加氢二班 |  | Wafi
|  |  |  | 配合更换空呼气瓶 |  | 加2分 |  | 加氢四班 | 陈盈嬟 | Wafi

## 日检表
HSE Daily Checklist for No.2 Refining Department 炼油二部HSE日检表
check date 检查日期： 5 MM 27 DD inspector 检查人：毛奕清 江志宁 WAFI
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.5 Management of high risk work 高风险作业管理 | 5.5.1 Management of High Risk Work Permit 高风险作业许可管理 5.5.2 Scope of application of High Risk Work Permit 高风险作业许可证使用范围 5.5.3 Term of validity of High Risk Work Permit 高风险作业许可证有效期限 5.5.4 Approval of High Risk Work Permit 高风险作业许可证审批 5.5.5 High risk work application 高风险作业申请 5.5.6 Cancellation of High Risk Work Permit 高风险作业许可证取消 5.5.7 Closure of High Risk Work Permit 高风险作业许可证关闭 5.5.8 Completion of High Risk Work Permit 高风险作业许可证填写 5.5.9 Management of High Risk Work Permit for holidays and festivals (statutory holidays, Saturday and Sunday) 节假日（法定节日、周六、周日）高风险作业许可证管理 5.5.10 Filing and management of High Risk Work Permit 高风险作业许可证存档与管理 5.5.11 work at heightRequirements of high risk work 高风险作业要求 5.5.12 High risk operation guardian 高风险作业监护人 | Whether to implement the high-risk operation management system 是否落实高风险作业管理制度 | 今日现场无高风险作业
抽查作业票上监护人资格票号0018445，作业单位监护人与作业人为同一人。部门安全管理人员现场已经提出此问题。
| Safety Management System 安全管理制度 5.13 Energy isolation management 能量隔离管理 | 5.13.1 Requirements on energy isolation 能量隔离管理要求 5.13.2 Steps of energy isolation 能量隔离实施步骤 | Whether to implement energy isolation management requirements 是否落实能量隔离管理要求 | 无
| Safety Management System 安全管理制度 5.15 Management of portable gas detectors 便携式气体检测仪的使用管理 | 5.15.1 Operation Dept. shall establish portable gas detectors register and include portable gas detectors used by field operators into the management scope of duty shift to ensure they are well equipped and ready to be put into operation. 运行部负责建立本部门便携式气体检测仪台账，外操使用的便携式气体检测仪应纳入交接班管理。 5.15.2 The operation department shall organize training so that the operators can master the basic operation and correct use of the gas detection and alarm instrument. 运行部应组织培训，使操作人员掌握气体检测报警仪的基本操作、正确的使用方法。 5.15.3 Various Operation departments shall report any abnormal function of the portable gas detectors to measurement discipline of Power Dept. in line with the verification period for regular check-up of the instruments. Measurement discipline shall provide data and report for all the instruments which will be the base for HSE Dept. to decide whether they are to be discarded. 各运行部按检定周期报机械动力部-计量专业对便携式气体检测仪进行定期检定，检定合格、贴合格标贴后方能投入使用，计量专业对仪器提供的数据及报告，作为便携式气体检测仪报废的依据。 5.15.7 The portable gas detector should be worn close to the mouth and nose breathing area,such as the front neckline of clothes, and should not be placed in the pocket. 便携式气体检测报警仪的佩戴应接近口、鼻呼吸区域，如衣服前领口等，不得放置于口袋内等位置。 | Is the department's four-in-one alarm record accurate 部门四合一报警仪台账是否准确 | 已按时更新
|  |  | Is the department's four-in-one alarm device safe to check 部门四合一报警仪是否按时校验 | 按时校验
|  |  | Is the department's four-in-one alarm device damaged 部门四合一报警仪是否有损坏 | 无损坏
|  |  | Whether department staff use the four-in-one alarm device correctly 部门员工是否正确使用四合一报警仪 | 佩戴正常
|  |  | 公司岗检问题提醒：外操在涉硫化氢区域内未佩戴或未按要求佩戴四合一报警仪。巡检人员安全帽未系帽带，未佩戴报警仪。 | 佩戴正常
| HSE Comprehensive Management System HSE 综合管理制度 5.11 HSE signs HSE标识 | 5.11.2.2 （1）For safety sign, it shall implement relevant regulations in Safety Signs and Guideline for Use (GB2894) 安全标识应执行 GB2894《安全标志及其使用导则》的相应规定； 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE 标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | According to the results of on-site hazard identification, safety warning signs are reasonably set up, and the signs are hung in accordance with regulatory requirements. 根据现场危害辨识结果，合理设置安全警示标志，标志系挂符合规范要求 | 标识设置合理
|  |  | 公司岗检问题提醒：安全警示牌被污染，有损坏的标识牌。安全警示标识牌损坏褪色。“必须穿防护服”安全标志不准确，部分安全警示标志同一位置重复张贴。风筒风向标破损并被挂住，需要更换。 | 标识设置合理
|  |  | Whether there are damaged safety signs in the department's territory, and whether the posted location is reasonable 部门属地区域内是否有损坏安全标识牌，张贴位置是否合理 | 已全部整改
| HSE Comprehensive Management System HSE 综合管理制度 5.13 HSE management for contractors (suppliers) 承包商（供应商）HSE管理 | 5.13.9.2 The Department who the contractor is working for, and the professional department in charge shall carry out daily management of the contractors. Advice the contractors of safety precautions while working for the department, control their operating actions, and report any action that contradicts with HSE requirements to the HSE Dept. for their discipline. 承包商需求部门、专业主管部门负责对承包商进行日常 HSE 管理。对承包商为本部门服务过程安全注意事项进行告知，对承包商作业行为进行管控，对不符合 HSE要求行为报送 HSE 管理部进行处罚等管控措施； 5.13.9.3 The department involved shall manage contractors entering its area of responsibility, , review approve contractors entering its area of responsibility, monitor their works, deny access of any contractor that has not been authorized to its production area. 属地部门对于进入本区域承包商进行管控，负责对进入本区域的承包商作业进行审批及作业监护，对于未经批准的承包商，禁止其进入该生产区域。 5.13.9.4 All departments shall not designate any contractor to do any job that falls outside its scope of qualification. 各部门不得指派承包商从事超出其资质范围的其他作业。 | Whether to inform contractors about safety 是否对承包商进行安全告知 | ---------
|  |  | 公司岗检问题提醒：检查时未找到与承包商相关的安全培训记录、安全考试试卷或安全风险告知书等相关资料。3月20日承包商人员 Tan Kuan Xing有考试成绩，未能提供试卷。 | ---------
|  |  | 部门对承包商HSE培训时未包含硫化氢气体防护相关内容 | ---------
|  |  | Whether the department is aware of the scope of the contractor's qualifications for work; whether the assigned work is out of scope 部门是否知道承包商作业资质范围；所安排工作是否超出范围 | ---------
|  | 5.5.2.5 Requisition of PPE 防护用品领用 （1）Each department shall request for PPE based on the distribution standards via HSE PPE Statistic form, after approval from HSE Department, it is distributed to each departments from warehouse, if departments put forward an unplanned requirement, it is needed to apply through online process OA HYBN-0814—PPE Requisition, which is subject to the approval of the HSE Department, and PPE are collected and distributed; 各部门依据配备标准，通过HSE物资统计表上报至HSE部，经HSE管理部审批后仓库统一发放，部门如需提出计划外需求，需通过线上HYBN-0814流程《HSE物资申领流程》申请，经HSE管理部审批后领用发放； | Do employees know how to request personal protective equipment (PPE)? If PPE is damaged or needs replacement, do employees know how to report and request a replacement? After collection of PPE, does shift or dept ask employees to log the records? 员工是否知道怎么申请劳保物资？ 如果劳保损坏/更换，是否知道怎么上报更换？ 领取劳保后，班组/部门是否让员工签字？ | 清楚
在标液配制过程中，发现有一名员工未佩戴护目镜，尽管现场已张贴有腐蚀性警示标识
|  | 5.5.2.6 Persons entering into the production area or maintenance and overhaul site must wear qualified safety clothes, safety shoes, safety helmets, safety goggles and earplugs or earmuffs. Persons entering into special area shall corresponding labor protection supplies such as the gas mask and respirator. 进入生产区域或检维修现场，必须穿合格的劳保工作服、劳保鞋，戴好安全帽、防护眼镜和耳塞 或耳罩，特殊区域应佩戴防毒面具、呼吸器等相应的劳动防护用品 | Whether the labor protection products of the employees of the department are worn and used correctly. Whether the overalls are rolled up at the cuffs or open plackets. Whether the helmet is adjusted well, tighten the lower forehead strap. Does employee know which work activity requires what kind of PPE? 部门员工劳动防护用品是否正确穿戴、使用。工作服是否卷起袖口或敞开衣襟。安全帽是否调好帽箍，系紧下额带。 员工是否知道每项工作需要佩戴什么劳保物品？ | 现场巡检，作业人员劳动防护用品佩戴齐全
| Occupational disease prevention and control 职业病预防和控制 | 5.6.1.3 No labor protection measures shall be dismantled or deactivated without the consent of the HSE Dept. 未经HSE管理部同意，不得擅自拆除或停用职业卫生防护措施。 | Site inspection: Whether the occupational health protection facilities in the workplace are operating normally. 现场检查：作业场所各项职业卫生防护设施是否正常运行。 | 检查情况正常
|  |  | 公司岗检问题提醒：初馏塔中上部平台腰杆脱焊，移动式升降平台栏杆被拆除，T2转运站滚轮防护罩破损 公司岗检问题提醒：常减压P230B机泵密封冲洗油温度计打翻。 | 无异常
|  | 5.6.3.2 Treatment for toxic gas poisoning 有毒气体中毒处理 In the event of an accidental poisoning caused by toxic gas, rescuers shall properly wear appropriate PPE before removing poisoned people out of dangerous areas. They shall perform on-scene rescue upwind, notify first-aiders to come to the scene, and transfer those in severe condition to hospital for emergency treatment. 发生有毒气体中毒时，救（监）护人员应佩戴上适用的防护用具，立即将中毒人员脱离危险区，到上风口对中毒人员进行现场救护，同时通知急救人员到现场救助，严重者立即送医院抢救。 | Does the department have operating procedures for toxic gas exposure incidents, and are employees informed about them? 部门是否有有毒气体中毒的操作规程？是否对员工进行宣贯？ | 部门硫化氢可能扩散区域已张贴在外操室，中毒急救流程列入演练计划。
|  | 5.3.1.4 Abnormal wastewater discharge should be reported and approved by relevant de-partments before proceeding, and the "Wastewater Classification Control Management Pro-cedure" should be implemented. 异常排污应进行申报、相关部门审批后方可进行，执行《污水分级控制管理程序》。 | 1. Whether the abnormal discharge is reported as required. 2. Whether the abnormal discharge process is carried out in accordance with the approval requirements, such as discharge time, discharge volume, etc. 1.是否按要求申报异常排污。 2.异常排污过程是否按审批要求开展，如排放时间、排放量等。 | 无异常排污
|  | 5.3.1.5 It is strictly prohibited to discharge all kinds of waste water by dilution. 严禁采用稀释的方法排放各类废水。 | Check on-site to see whether production water, fire-fighting water, etc. are used to dilute discharged wastewater. 现场检查是否存在使用生产水、消防水等稀释外排废水的现象。 | 无异常排废水现象
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （6）All departments shall strengthen management to completely eradicate the occurrences of running, emitting, dripping and leaking. 各部门应加强管理，杜绝跑、冒、滴、漏现象发生。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.现场是否存在跑、冒、滴、漏现象。 2.是否针对跑、冒、滴、漏及时组织整改或制定预防控制措施。 | 无跑冒滴漏
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （4）All departments shall ensure that the sewage facilities can operate stably for a long pe-riod, which are not allowed to be dismantled or shut down without authorization. 各部门确保污水设施长周期稳定运行，不得擅自拆除或停运。 | 1. Whether the sewage facilities are operating normally. 2. Whether the removal or decommissioning of sewage facilities is applied for and approved in accordance with the system requirements, and whether control measures for the removal or decommissioning of sewage facilities are formulated and strictly implemented. 1.污水设施运行是否正常。 2.污水设施拆除或停运是否按制度要求进行申请和审批，是否制定污水设施拆除或停运控制措施并严格落实。 | 运行正常
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （8）The affiliated unit shall arrange the specially-assigned person or post to be responsible for the switching and collection of initial rainwater and clean rainwater. 所属单位应安排专人或专岗负责初期雨水与清洁雨水的切换与收集工作。 | 1. Whether there are leakage, bubbling, dripping or leaking on site. 2. Whether timely rectification or preventive control measures are formulated for leakage, bubbling, dripping or leaking. 1.是否制定初期雨水与清洁雨水切换工作要求。 2.抽查班组人员对初期雨水、清洁雨水切换工作掌握情况。 | 情况良好
|  | 5.3.2.1 （9）In case of any spillage of oils or other chemicals on the ground, it shall be disposed in a timely manner, which are strictly prohibited to be flushed into the sewage or rainwater system by the use of water. 油品或其它化学品洒落地面，应及时处理干净，严禁将用水冲入污水或雨水系统。 | 1. Check the clean conditions of the equipment and the ground on site, and check whether there is leakage. 检查现场设备和地面的卫生状况，是否存在跑冒滴漏的现象2. Whether the lubricants and other chemicals on site are properly stored 现场润滑油等化学品保存是否得当 3. Whether there are oil flowers in the rain gutter 雨水沟是否有油花。 | 雨水沟无油花。
|  | 5.3.2.1 （10）The affiliated unit shall strengthen the management on the sampling barrels and oil drip pans, inside which the waste oil shall be washed and dumped in time. The sampling bar-rels shall be covered to prevent the pollution of the rainwater system. 所属单位应加强现场取样桶、接油盘的管理，其内的废油要及时清倒，取样桶应加盖，以防污染雨水系统。 | 1. Is there any waste oil in the on-site sampling barrel and oil receiving pan that has not been emptied in time? 2. Are the on-site sampling barrels covered or other equivalent measures taken to prevent rainwater from eroding and polluting? 1.现场取样桶、接油盘是否存在废油未及时清倒。 2.现场取样桶是否加盖或采取其它等效措施防止雨水冲刷污染。 | 取样桶内无残油
|  | 5.3.2.1 （11）The affiliated unit shall strengthen the management on hazardous wastes and additives sheds to prevent them from polluting the rainwater system. 所属单位应加强危险废物与助剂棚的管理工作，防止其污染雨水系统。 | Check the site to see if there is any leakage at the hazardous waste and additive storage points. 查现场，危险废物与助剂存储点是否存在泄漏。 | 危废垃圾桶和助剂储存点无泄漏
|  | 5.3.2.1 （12）It is forbidden to pour various pollutants into a clean rainwater system; it is forbidden to transport or store waste water containing toxic pollutant by means of oily rainwater or clean rainwater ditches. 禁止将各类污染物倒入清洁雨水系统；禁止利用含油雨水、清净雨水沟渠输送或者存贮含有毒污染物的废水。 | Check the site and clean the stormwater system for oil and other contaminants. 查现场，清洁雨水系统是否存在油污和其它污染物。 | 无污染
|  | 5.3.2.1 （13）It is forbidden to discharge oils, acid liquor, alkali liquor or toxic waste liquid in high concentration to the drainage pipe network. 禁止向排水管网排放油类、酸液、碱液或者高浓度有毒废液。 | Is there any discharge of oil, acid, alkali and high-concentration toxic waste liquid (such as chemical cleaning waste liquid) into the oily sewage system? 是否存在向含油污水系统排油、排酸、排碱和高浓度有毒废液（如化学清洗废液）。 | 未发现异常排放
|  | 5.3.2.1 （14）The clean effluent that fails to reach the control index of discharged clean rainwater is strictly prohibited to be discharged into the rainwater system. 清净下水达不到外排清洁雨水控制指标，严禁排入雨水系统。 | In addition to the clean sewage that is normally discharged into the rainwater system, other clean sewage that is not normally discharged should be sampled and analyzed and only discharged into the rainwater system after it is found to be qualified. 除正常排放去雨水系统的清净下水外，其它非常规排放的清净下水是否取样分析且合格后再排入雨水系统。 | 已改至含油污水
|  | 5.3.2.1 （15）It is strictly prohibited to discharge the fresh water, steam condensate, boiler blow-down water, etc. into the production sewage system. 严禁将新鲜水、蒸汽凝结水、锅炉排污水等排入生产污水系统。 | Is there fresh water, steam condensate and boiler wastewater directly discharged into the production wastewater system? 是否存在新鲜水、蒸气凝结水和锅炉排污水直排进入生产污水系统。 | 未发现异常排放
|  | 5.3.2.1 （16）The affiliated unit shall regularly conduct a compete cleaning-up and desilting to the sewage wells, drainage channels and ditches, etc., to ensure that the drainage system is unblocked to prevent the overflow of sewage or the cross-flow of rainwater. 所属单位应定期对其污水井、排水沟渠等进行全部清理与清淤，保证排水系统畅通防止污水外溢或雨污水互串。 | Check the drainage block or not 检查排水沟通畅情况 | 检查通畅
|  | 5.3.2.1 （17）In case of any failure of the sewage treatment and transportation facilities, etc., the unit in charge of which shall timely repair them and put into use as soon as possible according to the procedures and report to the HSE Dept. If it cannot be repaired in a short time and causes the environmental control index of the pollutants discharged outwards exceeding the standard, it shall be disposed according to the relevant procedures of the emergency plan and even shut down in serious cases. 污水处理及输送设施等出现故障，所在单位应按程序尽快及时修复投用，并报告HSE管理部。短期不能修复，造成外排污染物环保控制指标超标的，按应急预案相关程序执行，情况严重进行停车处理。 | Whether the wastewater-related environmental protection facilities (online monitoring, lifting tank pump) are operating normally 废水相关环保设施（在线监控、提升池机泵）是否正常运行 | 正常运行
|  | 5.3.2.1 （18）The Quality Analysis Dept. shall collect the toxic and harmful waste water for analysis, which shall not be discharged into domestic sewage or waste water for laboratory test. 质量检验部应做好有毒有害分析废水的收集工作，不得将有毒有害分析废水排入生活污水或化验废水中。 | 1. Check whether the Quality Inspection Department has formulated management requirements for toxic and hazardous analytical wastewater. 2. Check the Quality Inspection Department's toxic and hazardous analytical wastewater treatment ledger or records. 1.查质检部是否制定有毒有害分析废水管理要求。 2.查质检部有毒有害分析废水处理台账或记录。 | 不涉及
|  | 5.3.2.1 （19）Any hidden danger of drainage and environmental protection accidents shall be elimi-nated immediately once found to ensure that the pollutants discharge reaches the standard. 发现排水环保事故隐患应立即进行消除，确保污染物排放达标。 | 1. Whether potential sewage discharge accidents are discovered and reported in a timely manner. 2. Whether measures are taken immediately to eliminate potential drainage and environmental protection accidents. 1.是否及时发现污水排放事故隐患并报告。 2.是否立即采取措施消除排水环保事故隐患。 | 无异常排放
2025年6月19日4:06至5:54，加裂装置含油污水池外送污水，经检查装置分级控制排放口水质统计台账和LIMS，均未发现相关分析记录。
|  | 5.4.1.3 All types of waste gas must be discharged as per standard. 各类废气须达标排放。 | Check LIMS or waste gas online monitoring data, and find out the reasons and deal with them if the monitoring results or hourly average values ​​of various waste gases exceed the standards, and report them to the HSE Management Department in a timely manner. 查LIMS或废气在线监测数据，各类废气监测结果或小时均值超标，是否查明原因并处置，是否及时报告HSE管理部。 | 无异常排放
|  | 5.4.1.4 Waste gas treatment facilities, monitoring facilities and VOCs control facilities shall be well protected. No department or individual may shut down, idle or dismantle them without authorization. 废气处理设施、监测设施、VOCs控制设施应保护完好，任何部门和个人不得擅自停运、闲置、拆除。 | 1. Check the site to see whether the waste gas treatment facilities and monitoring facilities are operating normally, and whether they have been shut down, idled or dismantled without permission. 2. Check the maintenance records to see whether the waste gas treatment facilities and monitoring facilities are calibrated and maintained regularly. 1.查现场，废气处理设施、监测设施是否正常运行，未经许可是否存在停运、闲置和拆除情况。 2.查维护记录，是否定期对废气处理设施、监测设施校验、维护。 | 检查正常
|  | 5.4.1.5 Effective disposal measures must be taken to the malodorous gas which can be emit-ted only when reaching the emission standard for malodorous pollutants. 恶臭气体必须采取有效的处置措施，达到恶臭污染物排放标准方可排放。 | 1. Check the site to see if the odor treatment facilities are operating normally. 2. Check LIMS to analyze the reasons for the excessive emission of odor pollutants, and optimize the process (including upgrading and transformation) or management to achieve standard emission. 1.查现场，恶臭处理设施是否正常运转。 2.查LIMS，恶臭污染物排放标准超标是否分析原因，并针对原因进行工艺（包括提标改造）或管理优化，实现达标排放。 | 无异常排放
|  | 5.4.1.6 In special circumstances where the flare system must be arranged, it must be notified to the Scheduling & Dispatch Dept. and the HSE Dept. Under the accident state, effective measures must be taken at the same time to completely burn the toxic and harmful gases to ensure that no environmental pollution accidents will occur. Meanwhile, the level of the sour gas flare liquid separating tank shall be strictly controlled to prevent the sour gas with liquid caused by too high level. 特殊情况一定要排火炬系统的，必须告知计划调度部、HSE管理部。事故状态下，须同时采取有效措施使有毒有害气体完全燃烧，确保不发生环境污染事故，同时严格控制酸性气火炬分液罐液位，防止液位过高导致的酸性气带液。 | 1. Check the site to see if the torch has any odor, black smoke, or acidic gas with liquid. 2. Check the operating procedures to see if the Port and Reserve Department has formulated and strictly implemented control measures to prevent incomplete combustion of toxic and harmful gases, black smoke, and acidic gas with liquid. 1.查现场，火炬是否存在异味、冒黑烟、酸性气带液问题。 2.查操作规程，港储部是否制定防有毒有害气体不完全燃烧、冒黑烟、酸性气带液控制措施并严格执行。 | 烟气无异常排放
|  | 5.4.2.1(5) Where the production, transportation, loading/unloading and storage will emit toxic and harmful gases or dust materials, the sealing, purification or other protection and treatment measure must be taken. 生产、运输、装卸、贮存能够散发有毒有害气体或者粉尘物质的，必须采取密闭、净化或其他防护与治理措施。 | Whether on-site leaks are repaired in time and whether there is any peculiar smell 现场漏点是否及时修复及有无异味 | 现场无漏点
| Waste management 废弃物管理 | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Whether to establish a sound solid waste collection and disposal management ledger 是否建立健全固废收集和处置管理台账 | 危废台账及时更新
|  | 5.5.1.1 The classification of solid wastes shall be based on the types of wastes, their components and the relevant requirements for treatment and disposal methods for collection, which shall be as beneficial as possible for the subsequent processing of solid wastes. Fol-lowing principles shall be observed: 固体废物分类应根据废物的种类、组分以及处理处置方法的相关要求进行收集的方式，应尽量有利于固体废物的后续处理。 | 1. On-site inspection of whether hazardous waste and general waste are collected separately 现场检查危险废物和一般废物是否分类收集 2. Whether the solid waste collection barrel is positioned 固废收集桶是否在定位摆放 （1）The hazardous wastes and the general wastes shall be collected separately; 危险废物和一般废物分开收集； （2）The recyclable materials and the non-recyclable materials shall be collected separately; 回收利用物质与不可回收利用物质分开收集； （3）The liquid wastes and the solid wastes shall be collected separately, and so forth; 液态废物和固态废物分开收集等。 | 检查正常
|  |  | 公司岗检问题提醒：危险废物收集、储存管理不善，废润滑油堆放处地面被润滑脂和吨桶渗漏的废油污染。一般废物桶内发现丙烯酸喷漆罐危险废物，湖水生活垃圾桶旁边有废金属（金属桶），污泥脱水室危险废物桶内有生活垃圾（饮料瓶、果皮）、废金属等。含油垃圾与一般固废混放，现场吨袋有渗漏，油品污染地面。危险废物垃圾桶出现老化开裂，内部储存的含油吸油粘等危废渗漏液会导致周边土壤受到污染。 | 垃圾已按要求分类，部分危废桶中吸油毡使用率过低，请节约资源，合理使用
|  | 5.5.2.4 The waste management ledger shall be established. 建立废弃物管理台账。 | Check the waste management ledger. 1. Whether the waste management ledger has been established. 2. Whether the content of the waste management ledger meets the requirements. 查废弃物管理台账。 1.是否建立废弃物管理台账。 2.废弃物管理台账内容是否满足要求。 | 按公司要求执行
|  | 5.5.2.7（2）The ground surface of storage sites for hazardous wastes shall be hardened and pro-vided with anti-seepage treatment. The sites shall be equipped with canopies, cofferdams or fences; waste water discharge guiding pipelines or channels shall be provided, and the waste water shall be disposed in the Company’s waste water treatment facilities. 危险废物的贮存场所地面应作硬化及防渗处理。场所应有雨棚、围堰或围墙；应设置废水导排管道或渠道，废水应进入公司废水处理设施处理。 | 1. Whether the ground of the storage site of hazardous waste is treated with anti-seepage treatment 危险废物的贮存场所地面是否做防渗处理。 2. Is there any leakage liquid collection facility for storing liquid or semi-solid waste? 贮存液态或半固态废物是否设置泄漏液体收集设施。 | 使用危废垃圾桶收集，无泄漏
|  | 5.5.2.7（4）Containers carrying hazardous waste shall be in perfect condition. 装载危险废物的容器应完好无损。 | Check the scene to see if the containers of hazardous waste are damaged or leaking. 查现场，装载危险废物的容器是否存在破损、渗漏。 | 危废垃圾桶无破损
|  | 5.5.2.8 （1）Management on general industrial solid wastes: the department that temporarily gener-ates a large amount of general wastes shall apply to the HSE Dept. which will entrust the dis-posal unit for collection and transportation. 一般工业固体废弃物管理：临时产生大量一般废物的部门向HSE管理部提出申请，HSE管理部委托处置单位进行收运处理。 | Check the site to see whether the large amount of general solid waste generated temporarily has been applied for transfer to the HSE Management Department as required. 查现场，临时产生的大量一般固废是否按要求向HSE管理部提出转移申请。 | 按公司要求执行
|  | 5.5.2.8（2）Management on hazardous wastes: as for those hazardous wastes with no recovery value, it is the generating unit that shall initiate a 0825 process for waste disposal through the OA. After the approval is completed, the HSE Dept. shall propose a disposal plan to the hazardous waste disposal company. 危险废弃物管理：对于无回收价值的危险废弃物，由产生装置提报废弃物处置申请流程0825，HSE管理部向危险废弃物处置公司提出处置计划。 | Whether the disposal of solid waste is declared 固废废弃物处置是否进行申报。 | 按公司要求执行
|  | 5.5.2.9（4）1)After the generation of hazardous wastes, the team or group on duty shall immediately sort and classify the hazardous wastes and store them in separate storage containers. 在危险废物产生后，当班班组立刻将危险废物拣开、分类，分别存放在单独贮存容器。 | 1. Check the team members to see if they are aware of the hazardous waste management procedures. 2. Check the site to see if the team has classified and stored the hazardous wastes separately as required. 1.抽查班组人员，是否知晓危险废物管理程序。 2.查现场，班组是否按要求将危险废物分类，分别存放。 | 今日未抽查
炼油二部职业健康专业风险评估工作已顺利完成，相关培训亦已开展。然而在抽查两名员工时，发现他们对培训内容不清楚，反映培训成效有待加强。
检查部门加氢精制班组年度危险源辩识培训情况，班组知道年度危险源辩识资料获取途径，但对具体内容不太清楚，岗位中度以上风险不知道。
|  | 5.5.2.9（4）3)Hazardous solid wastes generated intensively: corresponding packaging, transportation, stor-age and disposal plans shall be formulated for hazardous wastes generated intensively such as waste catalysts, waste clay, waste fillers, waste activated carbon, etc. 集中产生的危险固体废物：废催化剂、废白土、废填料、废活性炭等集中产生的危险废物应制定相应的包装、运输、贮存及处置方案。 | 1. Check the plan to see whether the corresponding packaging, transportation, storage and disposal plans have been formulated for the hazardous solid waste generated in a centralized manner. 2. Check the site to see whether the hazardous solid waste generated in a centralized manner is implemented in accordance with the plan. 1.查方案，集中产生的危险固体废物是否制定相应的包装、运输、贮存及处置方案。 2.查现场，集中产生的危险固体废物是否按方案内容执行。 | 按公司要求执行
|  | 5.5.2.9（4）4）The collection, transportation and disposal of liquid or semi-oil hazardous wastes, such as waste oil, sludge, oil residues and waste sulfolane shall be provided with special programs to ensure that the liquid waste will not leak or pollute the ground, and the waste oil, sludge, waste solvents, etc. that are sorted out shall be safely sent to the coal power station for incin-eration disposal. 液态或半油态的危险废物，如废油、油泥、油渣以及废环丁砜等的收集、运输及处置应有专项的方案，确保液体废物不泄漏、不污染地面，清理出的废油、油泥、废溶剂等应安全送至煤电站进行焚烧处置。 | 1. Check the plan to see if there is a special plan for liquid or semi-oil hazardous waste. 2. Check the site to see if there is leakage or ground contamination during the transportation of liquid or semi-oil hazardous waste. 1.查方案，液态或半油态的危险废物是否制定专项方案。 2.查现场，液态或半油态危废运输是否存在泄漏、污染地面情况。 | 按公司要求执行
|  | 5.5.2.9（4）5）The waste liquid from the laboratory of the Quality Analysis Dept. shall be collected by classification be sorted & disposed in accordance with composition. 质量检验部化验室废液应分类收集，分质处理。 | Check the site to see if the quality inspection department collects and classifies the waste liquid for testing. Check the waste management records to see if the waste liquid for testing is treated by quality. 查现场，质检部是否分类收集化验废液。 查废弃物管理台账，化验废液是否分质处理。 | 按公司要求执行
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.3 No one shall arbitrarily damage, embezzle, dismantle, stop using, bury, occupy and block fire fighting equipment, facilities and appliances. It’s prohibited to take fire hydrants, fire monitors and hydrant pipelines as supporting points or force-bearing points. 任何人不得擅自损坏、挪用、拆除、停用、埋压、圈占、遮挡消防设备设施及器材；禁止将消火栓、消防炮、消防管线等作为支撑点或受力点。 | 1、Are all firefighting equipment, facilities and instruments in a complete and ready state (whether they are damaged, misappropriated, dismantled, decommissioned, buried, occupied, blocked, etc.) 所有消防设备设施及器材是否处于完整备用状态（有无损坏、挪用、拆除、停用、埋压、圈占、遮挡等现象） 2、Whether fire hydrants, fire monitors, fire pipelines, etc. are used as support points or stress points; 是否存在将消火栓、消防炮、消防管线等作为支撑点或受力点等现象； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.4 It’s prohibited to narrow down the fire separation distance and arbitrarily block and occupy fire-fighting accesses. It’s forbidden to close or block escape routes and safety exits, to move, embezzle and damage any kind of fire safety signs at will. 禁止缩小防火间距，不得随意堵塞、侵占消防通道；禁止封闭、堵塞疏散通道、安全出口；禁止擅自移动、挪用、损坏各类消防安全标识。 | 1、 Whether all fire exits are kept clear; 所有消防通道是否保持畅通； 2、 Whether there are phenomena such as narrowing the fire separation distance, randomly blocking and encroaching on fire escapes, closing and blocking evacuation passages and safety exits; 是否存在缩小防火间距，随意堵塞、侵占消防通道，封闭、堵塞疏散通道、安全出口等现象； 3、 Whether all fire safety signs are complete and easy to use, and whether replacement records are kept;所有消防安全标识是否健全，并完整好用，有无做好更换记录； | 检查情况良好
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.5 Fire bank shall be complete and intact. If there is any construction, the fire bank shall be restored after the construction is completed and report to the department in charge and the competent department for acceptance. 防火堤应完整无缺，如有施工应经主管部门审批，施工结束要及时恢复，并向所在部门及主管部门申请验收。 | 1、Whether the fire bank are intact; 防火堤是否完整无缺； 2、If there is any construction, whether it has been approved by the competent department, whether the approval procedures are complete and records are kept and archived; 如有施工是否经主管部门审批，审批手续是否齐全并留有记录，存档管理； 3、If construction is required, whether the work is resumed in time after the construction is completed, whether the relevant departments and competent departments have applied for acceptance and whether records have been kept and archived; 如有施工需要，在施工结束后是否及时恢复，有无申请所在部门及主管部门验收并留有记录，存档管理； | 记录已完善
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.6 All kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials, shall be used exclusively for special purposes. All these materials shall be in a standby state instead of being vented, removed, reduced or damaged. 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资，做到专物专用，不得放空、撤除、减少或损坏，应时刻处于备用状态。 | 1、Whether all kinds of fire extinguishers, fire shovels, fire buckets, fire sand, fire blankets and other materials are used for their designated purposes and must not be emptied, removed, reduced or damaged; 各类灭火器、消防锹、消防桶、消防沙、灭火毯等物资是否做到专物专用，不得放空、撤除、减少或损坏； 2、Are all equipment and facilities complete and usable and always in standby status? 所有设备设施是否完整好用，并时刻处于备用状态； | 检查正常，处于备用状态
加氢SG 11020消防栓门把手损坏
加裂文方员工对二氧化碳灭火器使用不熟悉
| 5.2 Fire safety management requirements 消防安全管理要求 | 5.2.8 The Company’s firefighting systems, such as the stable high pressure fire water system,the foam fire extinguishing system, the sprinkler system, the fire automatic fire alarm system,the FGS system, the gas fire extinguishing system, the dry powder fire extinguishing system and other such systems shall be in the “automatic” mode, If any of the system cannot beautomatically started, then the personnel on duty shall start it manually. Upon the ending of an emergency, relevant departments in charge shall inspect, test and maintain the systems and adjust the systems back to the “automatic” mode. 公司消防系统如：稳高压消防水系统、泡沫灭火系统、喷淋系统、火灾自动报警系统、FGS 系统、气体灭火系统、干粉灭火系统等，日常应设置在“自动状态”，未正常启动时，值班人员应紧急采取手动方式启动；应急状态解除后，管理部门应对系统进行检查、测试和保养并恢复“自动”状态。 | Whether the fire protection systems are set to automatic state, and whether there are relevant inspection, testing, maintenance and other records in daily management. 消防各系统是否设置在自动状态，日常管理中有无相关检查、测试、保养等记录。 | 防火台账检查正常
| 5.3.6 Management of the automatic sprinkler system 自动喷水系统管理 | 5.3.6.2 Each department is responsible for the daily management of the automatic sprinkler system, and patrol inspection of the system shall be preformed once a day. 各部门负责辖区内自动喷水系统的日常管理，每天对系统进行1次巡查。 | Daily management of the automatic sprinkler system within the jurisdiction, whether the system is inspected once a day, and whether the relevant inspection records are complete; 辖区内自动喷水系统的日常管理，是否每天对系统进行1次巡查，相关巡检记录是否健全；
| 5.3.8 Management of fire hydrants, fire monitor, water pump adapters, fire standpipes and firehydrant boxes. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的管理 | 5.3.8.2 Each department is responsible for the daily inspection of fire hydrants, fire monitor, water pump adapters, fire standpipes and fire hydrant boxes under its jurisdiction. 各部门负责辖区内消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的日常检查。 5.3.8.3 The Equipment maintenance department is responsible for the maintenance and replacement of fire hydrants, fire monitors, water pump adapters, fire standpipes, and fire hydrant boxes. The equipment maintenance department is responsible for anti-corrosion, oiling, etc. and the department is responsible for it. 消火栓、消防炮、水泵接合器、消防竖管、消火栓箱等设备设施的维修、更换由属地部门提出需 求，再由设备检修部负责。 | Whether each department conducts daily inspections of relevant fire-fighting equipment and facilities within its jurisdiction as required, whether relevant records are complete, whether damaged facilities are maintained as required, and whether sound maintenance records are established. 各部门是否按要求对辖区内的相关消防设备设施进行日常检查，相关记录是否齐全，是否按照要求对损坏的设施进行维护保养，是否建立健全维修保养记录。 | 已按要求记录
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.1 Small fire-fighting appliances include all kinds of fire extinguishers, fire shovels, buckets, sand and blankets, and other materials. All these materials shall be used exclusively for special purposes, and shall not be appropriated for any other purpose or be vented, removed, reduced or damaged. 小型灭火器材包括各类灭火器、消防锹、消防桶、消防用沙、防火毯等，做到专物专用，不得挪作他用或无故放空、损坏、撤除。 5.3.9.2 Each department shall establish an account for the management of small fire-fighting appliances, which is managed and taken charge by specially-assigned personnel. 各部门应建立小型灭火器材管理台帐，专人管理及负责。 | Whether the small fire extinguishing equipment management account has been established, with a dedicated person to manage and be responsible for it 是否建立小型灭火器材管理台帐，专人管理及负责 | 台账正常
|  |  | 公司岗检问题提醒：消火栓箱SG13030门把手损坏，水带发霉老化等 | 正常
| 5.3.9 Management of small fire-fighting appliances 小型灭火器材管理 | 5.3.9.3 Appliances shall be placed in a places where they can be easily spotted and operated without affecting safety evacuation. The used appliances shall be immediately supplemented and replaced, and the site for these appliances shall not be moved at will. 器材应放置在显见易操作之处，不得影响安全疏散；使用过的器材应及时补充、更换，设置地点不得随意挪动 5.3.9.4 Inspect the small fire-fighting appliances no less than twice a month. 小型灭火器材检查每月不少于2次。 5.3.9.5 Fire sand shall be kept dry, buckets and boxes shall be intact, and the fire shovels shall be fully equipped. All these appliances shall be available at any time. 消防沙保持干燥，桶、箱应完好无损、消防锹配备齐全，随时可用 | Whether the equipment is placed at the setting point and whether the equipment is replaced and replenished in time after use; check at least twice a month to ensure that all types of fire-fighting equipment are in good condition and ready for use and the records are complete. 器材是否放置在设置点，使用后的器材是否及时更换补充；每月检查不少于2次，确保各类消防器材完好备用并记录完整。 | 已按要求检查无漏检
| 5.3.10 Coding for fire-fighting equipment and facilities 消防设备设施编码 | 5.3.10.3（3）Each department shall count the number of fire fighting equipment and facilities, and number these equipment and facilities as per the coding requirements. 各部门要统计本部门消防设备设施数量，按编号要求，对消防设备设施进行编号。 （4）Each department shall incorporate the inspection of code tags in their daily inspection. If any damage is found or the fonts are too ambiguous to be recognized, requirements for a new tag shall be put forward to the HSE Dept. which will make contacts for the production. 各部门要将编码标牌纳入日常检查内容，发现损坏或字体模糊无法辨认的，及时提出制作要求，由HSE管理部统一联系制作。 | Whether the fire-fighting equipment and facilities in the jurisdiction are managed by number, and whether the code signs are replaced in time if they are damaged or the fonts are blurred and unrecognizable; 辖区内消防设备设施是否进行编号管理，编码标牌发现损坏或字体模糊无法辨认的，是否进行及时更换； | 编号正常，存在大量手写编号
| 5.3.13 SCBA Usage and Inflation Room Management SCBA 和气瓶充气间管理 | 5.3.13.1 Each department conducts a comprehensive inspection of the SCBA (self-contained breathing apparatus) twice a week to ensure that the pressure of the regular used cylinder shall not be less than 15MPa, backup cylinder pressure shall not be ess than 25MPa, and that there is no obvious damage or defect in the components such as the full cover, breathing valve, pressure reducing valve, and straps. 各部门每周对SCBA（自给式呼吸器）进行两次全面检查，确保常用空呼气瓶压力不得低于15Mpa，备用空呼气瓶压力不得低于25Mpa，全面罩、呼吸阀、减压阀、背带等部件没有明显的损伤或缺陷。 5.3.13.2 When using SCBA, stay calm and follow the training procedures. 在使用SCBA 时，应保持冷静，按照培训的程序操作。 | Whether the department conducts comprehensive inspections of SCBA (self-contained breathing apparatus) twice a week as required, and whether the inspection records are complete; 部门是否按要求每周对SCBA（自给式呼吸器）进行2次全面检查，检查记录是否齐全； | 检查记录正常
|  |  | 公司岗检问题提醒：外操室检查空呼压力低， | 检查外操空呼检查记录，情况良好。
|  |  | Can personnel operate SCBA accurately? 人员是否会准确操作SCBA（空呼） | 空呼佩戴近期已全面检查一遍
| 5.3.14 Maintenance, suspension, demolition, abandonment and interlock removalmanagement of fire-fighting prevention system equipment and facilities. 消气防系统设备设施维修、停用、拆除、报废、联锁摘除管理 | 5.3.14.2 No one shall stop the working of fire fighting equipment and facilities. 禁止任何人擅自停用在用的消防设备设施。 5.3.14.3 Special demolition scheme shall be prepared and countersigned by competent authorities for the dismantling of the foam stations, fire monitor systems in the dock, fire alarm systems and other fixed large fire fighting equipment and facilities. And the demolition shall be made after the approval of the leader in charge of the company. The replacement of fire hydrants, fire monitors and other small equipment arising from damaging shall be made as per relevant provisions of this System. 对于泡沫系统、码头消防炮系统、火灾报警系统等固定式大型消防设备设施的拆除应编制专门的拆除方案，并经专业主管部门会签，经公司主管领导批准后方可拆除。对于消火栓、消防炮等小件设备损坏更换按本制度相关条款执行。 | Whether the department has arbitrarily stopped using the firefighting equipment and facilities in use; Whether a special demolition plan has been prepared for the demolition of large fixed firefighting equipment and facilities; whether small equipment is damaged and replaced in a timely manner; whether it is strictly implemented in accordance with the company's relevant procedures; 部门是否存在擅自停用在用的消防设备设施； 对于固定式大型消防设备设施的拆除是否编制专门的拆除方案；小件设备损坏更换是否及时；是否严格按照公司相关流程落实； | 无停运消防设备设施
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.16.3 Department which applies for the use of fire-fighting water under normal conditions shall fill in the Application Form for Use/Suspension of Fire Water. The conditions for use shall be identified by Utilities Dept. or Port and Storage Dept. and approved by HSE Dept. After the Scheduling & Dispatch Dept. has put this application in record, the fire water can be used. The Utilities Dept. and the Port and Storage Dept. shall pay attention to the pressure of fire-fighting water during its use, and change to another fire pumps when necessary. 正常申请使用时，由申请部门填写《消防水使用/停用申请表》，经公用工程部或港务储运部确认使用条件，并经HSE管理部批准，到计划调度部备案后，方可使用。公用工程部或港务储运部在用水期间应关注消防水压力，必要时切换消防水泵供水。 5.3.16.4 After the use of fire-fighting water, the department which applies for use shall report to the on-duty dispatcher in time, who shall inform relevant department of the completion. 用水完毕后，申请部门应及时报告值班调度，由值班调度通知相关部门用水结束。 | Whether the application procedures for fire water use are clear and records are kept and archived; 是否清楚消防水使用申请手续，并留有记录，存档管理； | 按公司要求执行
|  |  | Check whether the fire water pipe network and valves in the area are leaking, and whether the valve well is in standby status;属地内消防水管网、阀门是否有渗漏现象，阀门井是否处于备用状态； | 按公司要求执行
|  |  | Whether the fire riser and fire monitor are drained promptly after use and are always in standby status; 消防竖管、消防炮使用后是否及时排水，时刻处于备用状态； | 阀门一开一关，时刻处于备用状态

## 周检表
HSE Weekly Checklist for No.2 Refining Department 炼油二部HSE周检表
check date 检查日期： 4 MM 24 DD inspector 检查人：毛奕清 江志宁
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
| Safety Management System 安全管理制度 5.3 HSE hidden danger identification HSE 隐患排查 | 5.3.3.6 All departments shall prepare hidden danger identification form based on their discipline characteristics and actual production conditions and continue to improve such form in practice. 各部门应根据专业特点和实际生产情况制定隐患排查表，并在实际应用中不断持续改进。 5.3.4.1 Control requirements 治理要求 （1）For general hidden danger, departments involved shall immediately organize rectification. 对于一般隐患，由属地所在部门立即组织整改。 （2）For any general hidden danger which can’t be rectified immediately, the department involved shall develop a risk precaution plan and rectification plan, and rectify such danger within a specified timeframe. 对于暂不能整改的一般隐患，由属地部门制定风险防范措施和整改计划，限期整改。 5.3.6.1 All departments shall establish Hidden Danger Identification & Control Account. 各部门应建立《隐患排查治理台账》。 5.3.6.2 The hidden danger treatment should be recorded according to the "HSE Hidden Danger Investigation and Management Ledger" to achieve closed-loop rectification. 隐患治理情况应按《HSE 隐患排查治理台账》进行记录，做到闭环整改。 | Does the hidden danger investigation table meet the investigation requirements 隐患排查表是否满足排查要求 | 本月加裂61个隐患，加氢49个隐患。隐患已整理并打印上交
|  |  | Whether the hidden danger investigation and management record is updated in time 隐患排查治理台账是否及时更新 | 已更新至最新版本
|  |  | Whether all staff are trained on hidden danger management 是否组织全员培训隐患治理情况 | 列入每月副班培训中
|  |  | Is the rectification carried out as planned 是否按计划整改 | 有条件的将立即整改
| Safety Management System 安全管理制度 5.4 Management of hazardous chemicals 危险化学品管理 | 5.4.2.2 The HSE management department shall supervise the establishment of hazardous chemicals ledger by all departments.. HSE 管理部监督各部门建立危险化学品台帐。 5.4.2.4 Each operation department must carry out targeted training on the knowledge of hazardous chemicals according to the hazardous chemicals involved in its own department,and staff shall be familiar with information on safety technology of hazardous chemical involved in the post to ensure stable operation and personal safety in production, storage, use, transportation and disposal of hazardous chemicals. 各运行部必须根据本部门涉及的危险化学品开展针对性的危险化学品知识培训，建立本部门《化学品普查表》与《危险化学品台帐》。员工应熟悉本岗位涉及的危化品安全技术信息，以保证危险化学品生产、储存、使用、运输、废弃处置等环节的平稳操作和人身安全。 5.4.2.5 Before using hazardous chemicals, the staff must know and grasp relevant MSDS andsafe operation instructions of hazardous chemicals, take relevant precautionary measures and prevent personal injuries. 员工使用危险化学品时，必须了解和掌握相应危险化学品安全技术说明书和安全操作规程有关内容，并采取相应的防范措施，避免发生人身伤害事故。 | Does the department have a hazardous chemicals register 部门是否建立危险化学品台账 | 已更新至最新版本（二部危化品台账）
|  |  | Whether to organize full-staff learning 是否组织全员学习 | 已放在外操室电脑供学习
| Safety Management System 安全管理制度 5.14.Hydrogen sulfide prevention 防硫化氢中毒安全管理 | 5.14.1 All departments shall set up eye-catching warning signs in both Chinese and English in places where hydrogen sulfide leakage may occur, and hydrogen sulfide warning signs shall be set up in eye-catching places in workplaces where hydrogen sulfide exists. A wind vane shall be set in the eye-catching position of the unit. 各部门在可能发生硫化氢泄漏的场所设置醒目的中英文警示标识，存在硫化氢的工作场所应在醒目位置设置硫化氢告知牌。装置醒目位置应设置风向标。 5.14.2 All personnel having access to hydrogen sulfide hazard area shall carry portablehydrogen sulfide alarms and protection devices as required. 所有进入可能存在硫化氢等有毒有害气体区域的巡检或作业的人员，必须佩戴相应的便携式气体检测仪和防护器具。集中作业时，作业小组应至少佩戴 1 台便携式气体检测仪。 5.14.3 The site concentration should be monitored at any time when the acid water, gas escape site, drain port, sampling port, storage tank metering port and other hidden parts are active. 在酸性水、瓦斯逸出部位、排液口、采样口、储罐计量口等隐患部位活动时，应随时监控现场浓度。 5.14.4 When entering hydrogen sulfide hazard area for patrol, operators shall conduct individual protection well and carry portable hydrogen sulfide alarm. In case of operation in hydrogen sulfide hazard area, it shall wear isolated respirator, set up warning signs around operation points and assign special personnel for monitoring. 员工在涉及接触硫化氢等有毒有害气体作业时，应做好个体防护，佩戴便携式气体检测仪和适宜呼吸防护用品，并有专人进行监护。 5.14.5 According to the working environment of different posts, all departments shall equip the operators with appropriate protective equipment. When the concentration of hydrogen sulfide is less than 50mg/m3, filter type anti-gas appliances can be used; When the hydrogen sulfide concentration is greater than 50mg/m3 or in the area where the medium leakage occurs and the concentration is unknown, isolated respiratory protective equipment should be used,and the gas supply device of the protective equipment should be placed on the upwind side. 各部门根据不同岗位的工作环境为作业人员配备适量适用的防护器材。当硫化氢浓度低于50mg/m3 时，可以使用过滤式防毒用具；当硫化氢浓度大于 50mg/m3 或在发生介质泄漏、浓度不明的区域内应使用隔离式呼吸防护用具，防护用具的供气装置应置于上风侧。 5.14.6 It is forbidden for any person to enter the area where hydrogen sulfide poisoning may occur without proper protective equipment, and it is forbidden to take off the protective equipment in the toxic area. 禁止任何人员不佩戴合适的防护器具进入可能发生硫化氢中毒的区域，禁止在有毒区内脱卸防毒用具。 5.14.7 When the hydrogen sulfide detection instrument alarms, the panel operator should remind the site personnel in time, the operator should wear protective equipment, check the leak point, prepare protective equipment and report to the superior, and evacuate the downwind personnel, prohibit all fire operations, quickly identify the cause of the leak and control the leak. 硫化氢检测仪器报警时，内操应及时提醒现场人员，作业人员应佩戴防护用具、检查泄漏点、准备防护用具并向上级报告，同时疏散下风向人员，禁止一切动火作业，迅速查明泄漏原因并控制泄漏。 5.14.8 Operation in hazardous places that may contain hydrogen sulfide, such as sewage wells and closed containers, shall be carried out in strict accordance with the management requirements of restricted Spaces of this system. 进入污水井、密闭容器等可能含硫化氢的危险场所作业，要严格按照本制度受限空间的管理要求执行。 5.14.9 When construction and maintenance personnel of contractors enter hydrogen sulfide hazard area to work, operation departments where they belong to shall organize construction contractors to conduct risk identification and notification of hydrogen sulfide hazards in operation area, and provide necessary protective devices and emergency rescue facilities. 承包商作业人员在涉及硫化氢等有毒有害气体环境中作业时，属地部门应对承包商作业人员进行硫化氢等有毒有害气体防中毒防窒息安全培训和安全交底，为其提供必要的呼吸防护器具和应急救护设施如正压式呼吸器，长管呼吸器等。 5.14.10 Any operator which is likely to come in contact with poisonous and harmful gases such as the hydrogen sulfide shall take trainings on poisoning and suffocation prevention and shall only take the job after being tested to be qualified. 凡可能接触硫化氢等有毒有害气体的操作人员，应接受防中毒、防窒息安全教育，经考核合格，方可上岗操作。 5.14.11 Departments that may have hydrogen sulfide leakage shall formulate emergency rescue plans and establish a first aid network, ensure that on-site first aid, evacuation and escort, and transport rescue channels are unblocked, conduct regular drills on emergency plans, and revise and improve them in time. 可能存在硫化氢泄漏的部门要制定应急救援预案并建立急救网络，保证现场急救、撤离护送、转运抢救通道畅通，对应急预案定期进行演练，并及时进行修订完善。 | Have employees been trained to prevent hydrogen sulfide poisoning 是否对员工进行防硫化氢中毒培训 | 已全员考试验收
Comprehensive Management 综合管理 | 5.2 HSE organization HSE 组织机构 | 5.2.2 Each department shall establish a safety management organization and establish the corresponding HSE Organization Ledger 各部门应建立安全管理组织机构，并建立相应的《HSE组织台帐》 | Whether the Organizational Ledger has been established and updated in a timely manner 是否建立了组织机构台帐，是否及时进行了更新 | 组织机构台账已建立，更新及时.
| 5.3 HSE policies and objectives HSE方针 | People-oriented, compliance with laws and regulations, community harmony, environmentfriendly, risk controllable. 以人为本、依法合规、社区和谐、环境友好、风险可控。 | Are employees clear about the company's policies, goals and commitments? 员工是否清楚公司方针目标与承诺 | 抽查沈伟，麦拉赫，漆小龙，全部答出来 |  |  |  | 一轮班 |  | 江志宁
| 5.4 HSE commitment HSE承诺 | 5.4.1 Abide by Brunei's laws and regulations, respect local customs and habits, and maintain a consistent attitude towards HSE in all business areas. 遵守文莱法律、法规，尊重当地风俗习惯，在所有业务领域对HSE的态度始终如一。 5.4.2 Care for life and health, protect the ecological environment, always adhere to zero tolerance for violations, and pursue the goal of zero injury, zero pollution, and zero accidents. 关爱生命健康，保护生态环境，始终坚持违章零容忍，追求零伤害、零污染、零事故的目标。 5.4.3 In order to ensure the achieve the goal, provide human, material and financial resources to support. 为保证目标的实现，提供人力、物力和财力等资源支持。 5.4.4 Regularly report HSE performance to the Brunei government, account for the needs of stakeholders such as investors, customers, and contractors, and actively accept supervision from all parties around us to achieve continuous improvement. 定期向文莱政府公布HSE业绩，关注投资者、客户、承包商等利益相关方需求，主动接受社会各界监督，实现持续改进。 | Are employees clear about the company's policies, goals and commitments? 员工是否清楚公司方针目标与承诺 | 抽查沈伟，麦拉赫，漆小龙，全部答出来
| 5.9 HSE meeting HSE 会议 | 5.9.2.3 Each department holds a regular HSE meeting once a week. 各部门 HSE 例会每周召开一次。 5.9.3.3 HSE regular meeting of each department 各部门 HSE 例会 （1） Communicate the requirements of HSE meetings at all levels of the company and the recent safety production situation of the company. 传达公司各级 HSE 例会的要求及近期公司安全生产形势。 （2） Arrange HSE work of the department, and solve HSE related problems in the work of each team and staff. 布置本部门 HSE 工作，解决各班组及员工工作中 HSE 相关问题。 | The content of the company's HSE regular meeting was carefully communicated. The HSE regular meeting of this department was held on time. 公司HSE例会内容认真传达 本部门HSE例会按时召开 | 公司例会内容交接班时进行宣贯，并将例会纪要发到群里；部门例会每月末按时召开
| 5.14 HSE assessment HSE考核 | 5.14.2 Each department shall refer to the Company's "Performance Appraisal Measures" or refine the performance appraisal system of its own department to assess, reward and punish the HSE work of its own department, and establish the HSE assessment reward and punishment ledger. 各部门引用公司《绩效考核办法》或细化为本部门绩效考核制度，对本部门的HSE工作情况进行考核奖惩，并建立 HSE 考核奖惩台帐。 | Department’s HSE assessment status 部门的HSE考核情况 | 已在日周月检表内体现
Comprehensive Management 综合管理 | 5.16 Accident and incident management 事故事件管理 | 5.16.4.1 Each operation department shall encourage its employees to report near-miss accidents, and organize investigations and analyses on the near-miss accidents to find out the root cause and prevent the reoccurrence of the accidents. 各运行部门应鼓励并奖励员工报告未遂事件，并组织对未遂事件进行调查、分析，找出事故根 源，预防事故发生。 | Did the department make any request on reporting nearmiss incident? 部门是否对未遂事件进行过要求 | 本周没有未遂事件
|  | 5.16.5.1 incident and accident management requirements 事故、 事件报告要求 After an operation department accident or incident occurs, the occurrence department shall immediately report to the dispatch room, the person in charge of the department and the HSE Management Department, and submit a Preliminary Report Form of Accident (Incident) to the HSE Department via email within 24 hours. 发生事件、运行部级事故后，发生部门应立即报告调度室、本部门负责人和 HSE 管理部， 24 小时内通过邮箱向 HSE 管理部提报《事故（事件） 初步报告表》。 | Whether departmental accidents have been reported as required 部门事故事件是否按要求进行了报告 | 本周无事故事件发生
|  | 5.16.6.1 Incident investigation 事件调查 Where the incident submitted to the "Accident (incident) Preliminary Report Form", the occurrence department shall organize the incident investigation within one week after the occurrence of the incident, prepare the incident investigation record form, and the department shall file the record. 凡提报《事故（事件）初步报告表》的事件，发生部门应在事件发生后一周内组织事件调查，编写《事故（事件） 报告表》 ， 报 HSE 管理部。 | Whether the department's accident incidents are investigated as required 部门事故事件是否按要求开展调查 | 本周无事故事件发生
事故事件台帐已经建立，台帐内容填写不全，维护不及时。
|  | 5.16.7.1 In the course of handling of accidents and incidents, the principles of “Four do not let go”, namely, not allowing any existence of unclear accident causes, not allowing any missing of punishment on accountable parties of the accident, not allowing any failure in implementing the rectification measures and not allowing any failure in mass education targeting relevant liable personnel. 事故、事件处理都要坚持“四不放过”原则，即事故原因未查清不放过、责任人员未处理不放过、整改措施未落实不放过、有关人员未受到教育不放过。 | For accidents in the department, has the department adhered to the "Four Do No-Let-Go" principle? For accidents in other departments of the company, has the department organized employees to learn? 对于部门的事故，部门是否坚持了四不放过原则，对于公司其他部门的事故，是否组织了本部门员工进行学习 | 本周无事故事件发生
|  | 5.5.2.3 Issuance of protection supplies 防护用品发放 （1）The operation department must, according to the requirements of work safety and prevention of occupational hazards, issue to employees PPE with different protection functions and record the issuance of PPE according to “One Person One Record” (See HYBN-T7-08-4001-2024-3 Template of PPE Issuing Records); 运行部门必须根据安全生产和防止职业性危害的需要，发给员工具有不同防护功能的劳动防护用品并按照“一人一卡” 做好劳动防护用品发放记录（参照HYBN-T7-08-4001-2024-3劳动防护用品发放记录模板）; | Whether to establish an employee PPE distribution ledger, whether the ledger is true and complete. 是否建立员工PPE发放台账，台账是否真实、完整。 | 台账已按要求建立，检查没问题
XXX部有劳保发放记录但未建立“一人一卡。要求部门按照“一人一卡”劳保发放记录落实。
检查时发现炼油二部已建立 “一人一卡” 个人防护用品发放记录，但未将新安全帽记录在内，要求部门整改。
|  | 5.6.3.1 Operation protection 作业防护 （1）Prior to operation, workplaces where toxic gases may be present shall be tested for toxic gas concentration; 作业前对可能存在有毒气体的工作场所进行有毒气体浓度检测； | Do employees know which toxic and hazardous gases are present in their department and the required protective equipment? 员工是否知道部门有哪一些有毒有害气体？是否懂需要用什么劳动防护用品？ Does management have a list of hazardous substances/MSDS list? Has it been shared to employees? Do employee know how to read/obtain information from a MSDS? 管理人员是否建立部门内部的有毒有害气体清单并做好内部宣贯？员工是否了解MSDS内容？ Does employee know what does IDLH means? 员工是否知道IDLH指什么？IDLH是英文Immediately Dangerous to Life or Health concentration的缩写，指的是直接致害浓度。 | 抽查3人回答良好
|  | 5.6.1.4 Employees who participate in poisonous and harmful operations must undergo occupational health education beforehand, keep records of Occupational Health training records (See HYBN-T7-08-4003-2024-1 Occupational Health Training Records) and be provided with effective PPE. 对参加有毒有害作业员工，必须事先进行职业健康教育，做好职业健康培训记录(见HYBN-T7-08-4003-2024-1职业健康培训档案) 并提供有效的劳动防护用品。 5.6.1.7 Occupational Health regular training materials should be recorded and accompanied with proper records (See HYBN-T7-08-4003-2024-1 Occupational Health Training Archives) and filed for storage. 职业健康专业定期学习材料应做好职业健康培训记录 (见HYBN-T7-08-4003-2024-1职业健康培训档案) 并做好存档。 | Check if training records have been established? 培训档案是否按照要求建立？ Check whether OH poster had been published and shared with employees on a timely basis and if records had been logged. 检查职业健康海报是否已及时发布并与员工分享，并查看是否有记录登记 | 本月健康简报已打印放置于外操室外墙上
|  | 5.6.2.1 Noise protection 噪声防护 （1）Employees must wear earplugs or earmuffs when they are exposed to workplaces with excessive noise (greater than 85 dB). 员工接触噪声超标 (大于85dB) 的作业场所，必须配戴防噪声耳塞或耳罩； | Are employees aware of noise exposure limits? 员工是否知道噪声超标指标？ If noise exposure exceeds limit, what should you do? 如果超标，是否知道要佩戴什么防护用品？ | 抽查提问两名文方员工回答正确
|  | 5.6.2.2 Noise monitoring 噪声监测 （1）Conduct monitoring of noise at workplaces and noise exposure of employees semiannually; 每半年对作业场所噪声及员工噪声暴露情况至少进行一次监测； | Do employees know the internal noise monitoring points within their department? 员工是否知道部门内部噪声监测点在哪里？ | 抽查1人回答不全
|  | 5.6.2.4 Hearing protection 听力保护 （1）According to local laws and regulations, employees at workplaces where there is excessive noise level of more than 85 db(A) should undergo annual audiometry testing to ascertain the impact of excessive noise exposure and to prevent long term hearing loss. 在噪音水平超过85dB(A)的工作场所工作的员工应接受年度听力测试，以确定过度噪音暴露的影响并防止长期听力损失。 | Are employees aware of the health effects of noise and the legal requirement for annual hearing tests? 员工是否知道噪声对健康的影响？是否知道法律法规要求一年做几次听力测试？ | 抽查提问1人没回答上来
|  | 5.6.6.2 When working with acids and bases, employees must wear acid and alkali resistant clothes and wear acid and alkali resistant gloves and glasses. Operation departments are responsible for maintaining the eye wash and emergency shower facilities on the production site. It is required to test the eyewash and emergency shower facilities once per week and to make regular inspection records (See HYBN-T7-08-4004-2024-1 Template of Eyewash and Emergency Shower Inspection Records). 接触酸碱操作时，岗位员工必须穿好防酸碱服，戴好防酸碱手套和眼镜。运行部门负责维护生产现场的洗眼器和水喷淋设施，要求至少每周一次对洗眼器和水喷淋设施进行测试，并做好定期检查记录工作 (见HYBN-T7-08-4004-2024-1洗眼器喷淋系统检查表)； | Check eyewash inspection records. 检查现场洗眼器工况及喷淋情况和部门检查记录。 Do employees know the monitoring frequency? 询问员工是否知道检查频次 | 已按要求检查签字
质检部洗眼器过滤网上积聚残留物，导致喷嘴堵塞。
|  | 5.6.7.1 Each operating department is responsible for the management of illumination in each workplace. Timely contact electrical department when lighting is insufficient. 每个运营部门负责管理每个工作场所的照明。照明不足时及时联系电气部门。 | Check illumination in each field operating room 检查外操室的照明 | 照明灯及手电筒完好备用
| Medical aid 医疗救护 | 5.8.1.1 First aiders will be provided with an individual identification card for easy recognition on site and in each work station. Site workers must display their first aider cards in the notice board on site, while for office workers, first aider cards must be displayed at designated notice boards. 急救人员将获得一张个人身份卡，以便在现场和每个工作站进行识别。现场员工的急救卡需在上 岗证公告栏展示，办公楼(含检维修楼、中控楼、集控楼等)需在制定公告栏展示。 | Check whether first aider card is displayed at designated notice board and if employee always bring their first aider card 检查急救员卡是否张贴在指定的公告板上，并确认员工是否随时携带急救员卡。 | 已贴在墙上
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （2）Inside each First Aid Kit shall be equipped with inspection form to list the necessary supplies and their quantities for easy inspection and replenishment. Refer to HYBN-T7-08-4005-2024-2 Template of First Aid Booklet. 每个急救箱内都要配备急救箱检查表，列出必备的用品及其数量，以方便检查和补充，详见HYBN-T7-08-4005-2024-2急救药箱记录表。 | Whether the list of supplies is paired according to the requirements and check for inspection records 急救药箱内容是否按要求配备并检查记录 | 已按要求做好检查
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （4）Oral medicines shall not be placed in the medical kit. 口服药不得放入药箱内。 | Whether the oral medicine is also in the first aid kit. 口服药是否也在急救药箱中 | 口服药不在药箱中
灵活焦化外操室有4包滤毒盒和6个半面罩已超过使用有效期。重整外操室(FAR3)急救药箱内存有口服药及过期医用手套。
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （5）The position of the medical kit shall be clear and visible indoors and there shall be a position indicator. The medical kit must not be locked and should be easily accessible during work. 医药箱位置在室内清楚可见，有位置标识指示，医药箱不得上锁并在工作期间易于取用。 | Check whether first aid kit has proper signage and indicator, if first aid kit is accessible or not 检查急救箱是否有正确的标识和指示，并确认急救箱是否易于取用 | 早上检查加氢药箱封条被打开，班组没反馈
|  | 5.7.5.3 Allocation and management of First Aid Kit 急救箱配置与管理 （6）Operating departments shall appoint department first aiders to check the condition of the first aid kit, quality and validity of the medicines once per month. If the medicines are inadequate or expired, such persons shall timely report to the HSE Dept. to apply for procurement, replenishment and replacement in time. 运行部门指定部门急救人员每月对急救药箱情况、药物的质量、有效期进行检查，不足或过期时 应及时向 HSE 管理部申请购买，及时补充、更换。 | Whether the first aid kit is checked regularly by department first aiders, whether the use record and the check record are complete 药箱是否被部门急救人员定期进行检查，使用记录及检查记录是否完整 | 检查合格
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.1 Education training requirements 教育和培训要求 | 5.10.1.2 All departments shall be responsible for preparing and implementing their own annual HSE education and training plans and establishing HSE training records. 各部门负责编制和实施本部门HSE年度教育和培训计划、建立HSE教育培训档案与HSE培训台帐。 | 按年度计划进行培训并存档
|  |  | 5.10.1.3 Personnel who have not passed the HSE training and examination shall not be employed. The eligibility criteria are that the test score exceeds 80% of the total score on the paper. 未经HSE培训考核合格的人员不得上岗。合格标准为考试分数超过卷面总分的80%。 | 上岗员工的安全考试成绩均为80分以上
|  | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.1 New employees in operation positions shall receive 3 level HSE training, the time is 72 academic hours, and the annual refresher training time is not less than 20 academic hours, and they can only take the post after passing the examination. 生产操作岗位新员工应接受三级HSE培训，时间为72学时，每年再培训时间不少于20学时，并经考试合格后方可上岗。 | 已按要求落实
|  | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.3 Employees subject to occupation mobility or job transfer or leaving their posts for more than six months shall receive HSE training at levels of operation dept. and team. 员工在公司内工作调动、转岗以及脱离岗位六个月以上者，应进行运行部、班组级HSE培训，经考试合格后方可上岗。 | 已按要求执行
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.3 HSE training for employees in operator role 操作岗位员工 HSE 培训 | 5.10.3.4 When the operation department adopts new processes, new technologies, new materials or uses new equipment, it shall conduct targeted safety training for the relevant employees. 运行部采用新工艺、新技术、新材料或者使用新设备时，应当对有关从业人员进行针对性的安全培训。 | 如有涉及将按要求执行
|  | 5.10.5 Team-based HSE activities 班组 HSE 活动 | 5.10.5.1 All departments shall conduct department-based and team-based HSE activities. 各部门应开展以部门、班组为单位的HSE活动。 | 本月副班培训已全部完成
|  |  | 5.10.5.2 Group HSE activities shall be studied intensively at least once a month, and the learning time shall not be less than 2 academic hours each time. The department's HSE activities shall be conducted once a month, with no less than 1 academic hour each time. 班组HSE活动每月集中学习不少于一次，每次学习时间不少于2学时。部门HSE活动每月1次，每次不少于1学时。 | 已按要求完成培训
5.10.5.3 HSE Management Department shall formulate HSE activity learning plan of team and group every quarter. On the basis of meeting the requirements of the company, each department may arrange the learning of production process safety management knowledge, emergency drills and other HSE related activities. HSE管理部每季度制定班组HSE活动学习计划。各部门在满足公司要求的基础上，可安排生产过程安全管理知识学习、应急演练及其他与HSE相关的活动。
|  | 5.10.5 Team-based HSE activities 班组 HSE 活动 | 5.10.5.4 HSE activities of the team shall be recorded in detail in the team HSE activity record, including personnel attendance, learning records, etc. 班组HSE活动情况应在班组HSE活动记录上详细记录，包括人员出勤、学习记录等内容。 | 活动记录已完成
抽查XXX班组《班组HSE活动学习记录》记录不规范，2024年12月12日班组记录，XXX未参加活动，未参加人员原因未填写。
炼油二部个别班组培训内容无消防板块
|  |  | 5.10.5.5 The department leader shall check the learning status of the team and sign the activity record book before the 10th of each month. The management personnel of HSE department shall conduct spot checks on HSE activities from time to time. 部门领导应对班组学习情况进行检查，并于每月10号前在活动记录本上签字，HSE部管理人员不定期对HSE活动情况进行抽查。 | 已按要求完成
HSE Comprehensive Management System HSE 综合管理制度 | 5.10 HSE Education, Training and Competency Building HSE 教育、培训和能力建设 | 5.10.6 HSE training for contractors and visitors 承包商及访客HSE 培训 | 5.10.6.1 Before contractor personnel enter the factory, the HSE Management Department will conduct Level I HSE training. Before entering the operation area of each unit, the Operation Department will conduct Level II HSE training. After the training, the contractors must pass the examination and conduct safety briefings before operation. Each operating department should keep training records. 承包商人员入厂前由HSE管理部实施一级HSE培训，进入各装置区域作业前由运行部实施二级HSE培训，培训结束经考试合格，作业前进行安全交底后方可作业。各运行部门应做好培训记录。 | 前期入场承包商培训记录完好
|  |  | 5.10.6.2 Visitors shall handle entry permits only when they have received entry training. 访客经入厂培训后方可办理入厂通行证。 | 后续涉及将按要求执行
|  | 5.10.6 HSE training for contractors and visitors 承包商及访客HSE 培训 | 5.10.6.3 Before the contractor and visitors enter the company, the reception department shall submit the corresponding safety training process from OA, and carry out the on-site training after receiving the approval. The contractor safety training should be applied for three days in advance, and the accurate information of the contractor personnel should be attached. 承包商及访客进入公司前，接待部门需从OA提交相应的安全培训流程，经批复后开展入厂培训。其中承包商安全培训需提前三天申请，并附承包商人员准确信息。 | 后续涉及将按要求执行
| Identification and evaluation of environmental factors 环境因素识别与评价 | 5.2.2.2 All relevant departments shall organize the personnel to identify the environmental factors that can be controlled or are expected to be exerted influence on from their activities, products and services, and to fill out the Form for Identification and Evaluation of Environ-mental Factors and feed it back to the HSE Dept. 各相关部门组织人员从其活动、产品、服务中识别出能够控制或可望施加影响的环境因素，填写《环境因素识别和评价表》并反馈到HSE管理部。 | Ask the department staff on the spot whether they are clear about the concept and identification of environmental factors, etc. 现场询问部门人员是否清楚环境因素概念及识别等 | 提问员工回答良好
|  | 5.2.7 Update of environmental factors 环境因素的更新 In case of any major change on the Company’s activities, products and services or any up-date of regulations and other requirements, all departments shall timely supplement and identify environmental factors and report to the HSE Dept. for evaluation of environmental factors to redefine the major environmental factors and conduct management on them. 当公司的活动、产品、服务发生较大变化或法规及其他要求更新时，各部门应及时对环境因素进行补充识别，并报HSE管理部进行环境因素评价，以重新确定重要环境因素并对其进行管理。 | Whether to carry out the environmental factor identification and evaluation work of the department in the current year, and whether to update the environmental factor identification and evaluation table and the list of major environmental factors in a timely manner 是否开展本部门当年度的环境因素识别和评价工作，是否及时更新环境因素识别和评价表和重要环境因素清单 | 环境因素识别已完成并上交
|  |  | Check whether the site is implemented according to the department's environmental factor list and the measures formulated 对照部门环境因素清单及制定的措施检查现场是否落实 | 已按要求落实
|  | 5.9.1.1 A comprehensive identification of environmental factors shall be carried out for device startup and shutdown as well as maintenance. 装置开、停工、检修应进行全面的环境因素识别。 | 1. Whether environmental factors are identified during the start-up, shutdown and maintenance of the device, and corresponding control measures are formulated. 2. Whether various control measures are implemented as required. 1.是否对装置开、停工及检修过程进行环境因素识别，并制定相应控制措施。 2.是否按要求落实各项控制措施。 | 已按要求做好识别
| Wastewater management 废水管理 | 5.3.1.1 All kinds of waste water must be tested to satisfied department control limit indicators formulated by the Company before discharge. 各类废水须经检测达到公司制定的分级控制指标后方可排放。 | 1. Whether the test is carried out in accordance with the annual environmental monitoring plan. 2. Check LIMS to see whether the discharge is carried out after the test results of the graded control indicators meet the standards, and whether the discharge does not meet the standards and whether to apply for abnormal discharge. 1.是否按照年度环境监测计划进行检测。 2.查LIMS，分级控制指标检测结果是否达标后排放，不达标外排是否申请异常排污。 | 含油污水化验分析登记正常。
|  | 5.3.1.6 Water Body Pollution Emergency Plan and Oil Spill Response Plan shall be prepared. 应当编制水体污染与溢油应急预案。 | 1. Whether the responsible units of each sewage outlet have formulated a plan to prevent water pollution and conduct regular drills. 2. Whether the Port and Reserve Department has prepared an oil spill emergency plan and conducted regular drills. 1.各污水外排口责任单位是否制定防水体污染预案，并定期演练。 2.港储部是否编制溢油应急预案，并定期演练。 | 已制定防污水污染预案
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 2）The operation department.: the drainage management system of the unit; the operation specifications and internal control process indicators; the diagram of drainage pipe network of the department (including: the layout of discharge point, discharge direction, the identifi-cation of sampling port, the pipe network for diverting wastewater from clean water, etc.) ; establish the waste water management ledger, etc. 运行部：本单位排水管理制度；操作规程、内控工艺指标；本部门排水管网图（应包括：排放点布置、排放去向、采样口标识、清污分流管网等）建立废水管理台帐等。 | 查资料： 1. Sewage discharge management system 污水排放管理制度 2. Drainage network diagram 排水管网图 3. Internal control process indicators 内控工艺指标（仅限在线分析仪表） 4. Wastewater management ledger 废水管理台账 | 三废管理细则已放置于外操室，员工清楚内容
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （3）Sewage treatment plants, sour water stripping units, etc. shall be in strict compliance with the operation specifications to ensure the up-to-standard discharge. 污水处理场、酸性水汽提等装置应严格遵守操作规程，确保达标排放。 | 1. Spot check whether the key operations of sewage treatment plants and acid water stripping devices have formulated operating procedures. 2. Spot check and verify whether the operations and indicator controls of each position of the team are carried out in accordance with the operating procedures. 1.抽查污水处理场、酸性水汽提装置的关键操作是否制定操作规程。 2.抽查、验证班组各岗位操作及指标控制是否按操作规程执行。 | 已按要求执行
|  | 5.3.2.1 Management on water body pollution during operation period 运行期水体污染管理 （5）All departments shall ensure that the drainage process is complete and in compliance with the requirements. It is forbidden to change the direction of pollution discharge without permission, and the drainage process may not be altered at will without approval. 各部门应确保排水工艺完整与符合要求，杜绝私自改变排污去向，未经批准不得随意变更排水工艺。 | Check whether the change in drainage process is carried out in accordance with the change management requirements and check the relevant change information. 变更排水工艺是否按变更管理要求执行，查相关变更资料。 | 暂无此方面变更
|  | 5.3.2.1 （20）Where the high-concentration waste water (such as the highly sulfur-containing, am-monia-containing, phenol-containing, acid-base sewage, etc.) needs to be discharged, the water volume and water quality shall be reported to the Scheduling & Dispatch Dept. and HSE Dept. and the downstream processing plant shall be contacted and given explanation about the situation at the same time to avoid impact on the sewage treatment plant. 高浓度废水（如高含硫、含氨、含酚、酸碱等污水）需排放时，应向计划调度部、HSE管理部报告水量、水质情况，同时与下游处理装置联系、说明情况，避免冲击污水处理场。 | Check the discharge of overlimt wastewater, and check the OA process of discharge. 检查超标废水产生情况，检查超标废水排放OA流程。 | 无废水超标情况
|  | 5.3.2.1 （21）All water discharged to the external environment must be analyzed to prove qualified before being discharged outwards. 所有排往外环境的水须经分析合格后方可外排。 | 1. Whether the water discharged to the external environment is sampled and analyzed according to the environmental monitoring plan. 2. Whether the monitoring items and monitoring frequency are implemented as required. 3. Whether abnormal analysis results are reported immediately and the causes of abnormalities are analyzed. 1.排往外环境的水是否按环境监测计划取样分析。 2.监测项目和监测频次是否按要求执行。 3.分析结果异常是否立即报告，并对异常原因进行分析。 | 无异常
|  | 5.3.3.6 The comparison between online monitoring data and manual monitoring data shall be conducted no less than once every quarter for the water quality online monitoring system. No unit or individual may dismantle, idle or alter the automatic monitoring equipment for pollution source. 水质在线监控系统每个季度应开展不少于1次的在线监测数据与人工监测数据的比对。任何单位和个人不得擅自拆除、闲置、改动污染源自动监测设备。 | 1. Whether the online monitoring data of the water quality online monitoring system is compared with the manual monitoring data every quarter, and check the comparison report or record. 2. Check the maintenance record of the water quality online monitoring system to see whether the calibration and maintenance are completed as required. 3. Check the integrity of the automatic monitoring equipment for sewage water quality and whether it has been dismantled, idled or modified. 1.每季度是否对水质在线监控系统开展在线监测数据与人工监测数据比对，查比对报告或记录。 2.查水质在线监控系统维护记录，是否按要求完成校验、维护。 3.查污水水质自动监测设备完好性，是否被拆除、闲置或改动。 | 已按要求登记
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.1 Regularly inspect the FGS system, evaluate the operating status of the system,record key parameters, compare historical data, and analyze the stability and performance of the system.定期对 FGS 系统进行检查，评估系统的运行状态，记录关键参数，对比历史数据，分析系统的稳定性和性能 5.3.3.2 Regular software updates and virus scans to ensure system security 定期进行软件更新和病毒扫描，确保系统安全性 | Whether the FGS system is checked regularly to ensure stable system performance, whether the software is updated and virus scanned regularly to ensure system security, and whether relevant records are complete. 是否定期对FGS系统进行检查，确保系统性能稳定，定期对软件进行更新和病毒扫描，确保系统安全性，相关记录是否齐全。 | FGS报警记录不全
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.3 Clean the dust on the surface of the equipment in time to ensure good heat dissipation of the equipment; check the integrity of the power cord and connecting cables to prevent failuredue to aging or damage 及时清理设备表面灰尘，确保设备散热良好；检查电源线和连接电缆的完好性，防止因老化或破损导致故障 | Check and maintain the equipment to ensure the integrity of system components and check whether maintenance records are complete. 是否对设备进行检查和保养，确保系统部件性能完整，检查保养记录是否齐全 | FGS未出现故障
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.4 When a system failure occurs, the possible cause of the failure is determined based on the failure phenomenon, and corresponding troubleshooting measures are taken promptly to ensure the stable operation of the system. 当系统出现故障时，根据故障现象判断可能的故障原因，及时采取相应的故障排除措施，保障系 统的稳定运行。 5.3.3.5 Regularly conduct comprehensive calibration and debugging of the system to ensure the accuracy of various parameters and eliminate errors caused by long-term operation 定期对系统进行全面校准和调试，确保各项参数准确，消除因长期运行导致的误差。 | Whether the fault is promptly eliminated when it occurs, whether the system is fully calibrated and debugged regularly to ensure that all parameters are accurate, and whether the maintenance records are complete; 是否在出现故障时，及时排除故障，是否定期对系统进行全面校准和调试，确保各项参数准确，维修记录是否齐全； | FGS未出现故障
| 5.3.3 FGS System management FGS 系统管理 | 5.3.3.6 Establish and improve system maintenance work records, including inspection content, fault diagnosis, component replacement and other information, and organize and archive them to facilitate subsequent inquiries and analysis. 建立健全系统维修保养工作记录，包括检查内容、故障诊断、部件更换等信息，并整理归档，便于后续查询和分析。 | Whether a sound maintenance record has been established and whether the record content is complete; whether monthly work suggestions are made for the system operation. 是否建立健全维修保养记录，记录内容是否完整；是否对系统运行情况提出月度工作建议。 | 4月7日 单个FGS报警关联声光号未补填写，上次已考核
| 5.5 Fire prevention inspections and hidden danger management 消气防监督检查和隐患治理 | 5.5.2 Rectification of hidden dangers 隐患整改 For the hidden dangers spotted during the fire inspection, the department concerned shall contact corresponding department and personnel for to tackle with them. Rectification of ordinary hidden dangers shall be performed by professionals organized by each department. Major hidden dangers shall be rectified after the discussion by HSE management committee, before which safety protection measures shall be implemented by the personnel of relevant departments. 对于防火检查中发现的隐患，由所在部门联系相关部门和人员进行处理。一般隐患由各部门组织专业人员进行整改；重大隐患经公司HSE管理委员会讨论后落实整改，整改前由有关部门人员落实安全防护措施。 | Whether hidden dangers found during fire prevention inspections have been rectified in a timely manner; whether problems that have not been rectified in a timely manner and major hidden dangers have been included in the hidden danger ledger and reported to the HSE Management Department in a timely manner. 防火检查中发现的隐患，是否及时落实整改；未及时落实整改的问题及重大隐患是否列入隐患台账，并及时上报HSE管理部。 | 已全部签字

## 月检表
HSE Monthly Checklist for No.2 Refining Department 炼油二部HSE月检表
check date 检查日期： MM DD inspector 检查人：毛奕清 江志宁
expertise type 专业类别 | Inspection elements 检查要素 | inspection content 检查内容 | Check point 检查要素 | Check description 检查情况 | check photo 检查照片 | Assessment opinion 考核意见 | Correction deadline 整改截止时间 | Responsibility team 责任班组 | responsible person 责任人 | inspector 考核人
Field Safety Management 现场安全管理 | Safety Management System 安全管理制度 5.2 Risk management 风险管理 | 5.2.1.4 Organize hazard identification and risk assessment of in-service equipment and facilities at least once a year; 每年应至少组织一次对在役设备设施的危险源辨识与风险评价； 5.2.1.5 Organize hazard identification and risk assessment of various work in normal production at least once a year; 每年应至少组织一次正常生产过程中各项作业活动的危险源辨识与风险评价； 5.2.1.9 In production and other relevant activities, all departments and their staff shall conduct hazard identification and risk assessment and control as per the specified time, period and method and be responsible for the results. 各部门及员工在从事生产作业和其它相关活动时，应按规定时间、周期、方法进行危险源辨识、风险评价和控制，并对其结果负责。 5.2.1.10 Each department shall sort out its own operation activities, equipment and facilities,and submit the list of operation activities and equipment of the department to the competent business department for review. 各部门梳理本部门作业活动与设备设施，报业务主管部门审核后形成本部门的作业活动清单与设备清单。 5.2.4.1 For identified risks, each department shall expressly define and establish the responsibility, scope, methods and requirements related to the risk management & control, and shall integrate the safety risk control and hidden hazard screening into the management of production process, and ensure the risks are under control through hazard identification, risk assessment, risk control and monitoring. 对于辨识出的风险，各部门应明确风险管理的职责、范围、方法及风险管控要求等，将安全风险管控和隐患排查治理融入生产过程管理工作，通过危害辨识、风险评估、风险控制及风险监控，保证风险处于受控状态。 5.2.4.2 All departments need to take immediate measures to control the huge risks assessed. Major risks require immediate or near-term management; Moderate risk management within 2 years. Governance should be in the order of elimination and replacement,engineering control, management measures, individual protection to choose governance measures. 各部门对于评价出的巨大风险，需要立刻采取措施治理；重大风险需要立即或近期治理；中等风险在 2 年内治理。治理应按照消除、替换、工程控制、管理措施、个体防护的顺序来选择治理措施。 | Whether the hazard identification and risk assessment are carried out on time 是否按时进行危险源辨识与风险评价 | 已按公司要求完成，并根据公司要求更改
|  |  | Whether to organize full-staff learning 是否组织全员学习 | 已在副班时组织学习
|  |  | Are the identified risks effectively managed 是否有效管控辨识出的风险 | 根据现场作业情况做好风险辨识
| HSE Comprehensive Management System HSE 综合管理制度 5.14 HSE assessment HSE 考核 | 5.14.2 Each department shall refer to the Company's "Performance Appraisal Measures" or refine the performance appraisal system of its own department to assess, reward and punish the HSE work of its own department, and establish the HSE assessment reward and punishment ledger. 各部门引用公司《绩效考核办法》或细化为本部门绩效考核制度，对本部门的 HSE 工作情况进行考核奖惩，并建立 HSE 考核奖惩台帐。 | Whether to transform and compile the HSE assessment system of the department 是否转化编制部门HSE考核制度 | 已按要求做好日周月检更新
|  |  | Whether to conduct assessment on violations of HSE regulations within the department 是否对部门内违反HSE制度的行为进行考核 | 有日周月检已囊括所有制度内容，并不断更新
|  |  | Have you established a record of HSE assessment rewards and punishments 是否建立HSE考核奖惩台账 | 已建立
| HSE Comprehensive Management System HSE 综合管理制度 5.15 Emergency Preparedness and Response 应急准备与响应 | 5.15.5.3 Emergency plans shall be revised once three years and such revision shall be recorded and filed. 预案至少每三年修订一次，预案修订情况应有记录、归档并备案。 5.15.6.1 Each department should train employees on emergency regulations, emergency plans, emergency skills, accident cases and other emergency nowledge, and record them in training files. When the emergency plan involves contractors, the contractors should be trained. 各部门应对员工进行应急法规、应急预案、应急技能、事故案例等应急知识进行培训，并在培训档案中进行记录，应急预案涉及承包商时，应对承包商实施培训。 5.15.6.2（2）As for onsite disposal plan, operation department shall exercise such plan at least once a month for each shift, including one onsite actual emergency exercise. 现场处置预案运行部每班每月演练不少于 1 次，其中必须包括 1 次现场实战应急演练。 5.15.6.6 At the end of exercise, all departments shall immediately complete Emergency Exercise Record. 各部门演练结束后，应及时填写《应急演练记录》。 | Whether it is revised in time 是否及时修订 | 公司已修订
|  |  | Whether relevant training is carried out 是否进行相关培训 | 已完成培训，培训进度副班学习内容可查
|  |  | Whether the drill is conducted as required 是否按要求进行演练 | 本月已完成6个班组演练
Comprehensive Management 综合管理 | 5.5 Compliance management 合规管理 | 5.5.3.1 All functional departments shall obtain HSE laws, regulations and other related requirements concerning all production & operation links of the Company from competent government departments and superior company in a timely manner. 各职能部门从政府主管部门和上级公司及时获取与公司生产经营各环节相关的HSE法律法规及其他有关要求。 | Is it carried out as required? 是否按要求开展 | 已按公司发布要求开展
|  | 5.5.3.2 All functional departments shall update and submit list of HSE laws, regulations and other related requirements applicable to themselves to HSE Dept. within one week prior to the end of half a year. 各职能部门应在每半年结束前1周内更新并向HSE管理部报送本部门适用的HSE法律法规及其他有关要求清单。 | Is it carried out as required? 是否按要求开展 | 已按公司发布要求开展
|  | 5.5.3.3 All functional departments shall identify and obtain HSE laws, regulations and other related requirements and communicate them to all related parties. 各职能部门应将识别、获取的HSE法律法规及其他有关要求传达到各相关方。 | Is it carried out as required? 是否按要求开展 | 已按公司发布要求开展
|  | 5.5.4.1 All functional departments shall include HSE laws, regulations and other related requirements into management systems related to their disciplines. 各职能部门应当将HSE法律法规及其他有关要求纳入到本专业相关管理制度中。 | Is it carried out as required? 是否按要求开展 | 已按公司发布要求开展
|  | 5.5.4.2 All departments shall implement HSE laws, regulations and other related requirements in a strict manner. 各部门应严格执行HSE法律法规及其他有关要求。 | Whether employees can obtain company notifications and department management systems in a timely manner 员工是否能及时获取公司通知与部门管理制度 | 公司及部门网站可查询
| 5.6.4 Ready for startup or commissioning 开车或投用前准备 | 5.6.4.2 Pre-Startup Safety Review applies to all HengYi existing production plants and new plants. Pre-startup safety review needs to be done for new plant completed before commissioning and for plant transformation project (including Major MOC) and overhaul before re-startup. PSSR开车前安全审查适用于恒逸所有现有生产装置和新建装置。新建项目完成后的投用、装置改造项目（含重大MOC）以及大检修后重新开车之前，需要进行开车前安全审查。 | Whether a pre-startup safety review has been conducted after maintenance or new construction of the unit 检修开工或新建装置是否进行了开车前安全审查 | 已按要求做好开车前检查，记录可查
Comprehensive Management 综合管理 | 5.7 Management of safety production information facilities 安全生产信息管理 | 5.7.1 Each department of the company shall collect and maintain HSE related information within its business scope, and ensure that relevant personnel (including contractor personnel) obtain the latest HSE information in a timely manner, so as to match the post risk control requirements. 公司各部门应收集、维护本部门业务范围内与HSE相关的信息，保证相关人员（包括承包商人员）及时获取最新的HSE信息，使其与岗位控制风险需求相匹配。 | Safety technical instructions and other production safety information collected by this department 本部门收集的安全技术说明书等安全生产信息 | 安全技能说明书齐全
| 5.8 Management of HSE facilities HSE设施管理 | 5.8.2.3 All departments shall conduct regular inspection of safety facilities and those required verification shall be verified by all competent departments periodically. 各部门应对安全设施定期检查，需校验的安全设施由各主管部门定期校验。 | Regular calibration of various instruments 各类仪表定期校验 | 已按要求做好检查
Change Management 变更管理 | 5.1 Change request 变更申请 | 5.1.1 The applicant shall designate a special person to be responsible for a change management work, and the person in charge shall initiate the change application. 申请单位应指定专人负责某一项变更管理工作，由负责人发起变更申请。 | Verify that a designated person is assigned to manage the change process and that they have initiated the change application. 确认已指派专人来管理变更流程并且该已发起线上变更申请。 | 谁发起谁负责变更
|  | 5.1.3 After the change department organizes the change risk assessment and implements the control measures, the person in charge shall initiate the online change application process, submit the change application to the competent department, and attach the change risk assessment and control measures results. 变更部门组织进行变更风险评估并落实管控措施后，由负责人发起在线变更申请流程，向主管部门提出变更申请，并附带变更风险评估及管控措施。 | Submitted the application with supporting documents. 提交申请并附上相关文件。 | 已按要求执行
| 5.2 Risk assessment 风险评估 | 5.2.1 The risk of change includes the risk during the implementation of change and the risk after the implementation of change. 变更的风险包括变更实施过程中的风险和变更实施后的风险。 5.2.2 All departments shall identify and evaluate the potential risks of changes before applying for changes. 各部门申请变更前应对变更的潜在风险进行辨识和评估。 | Check whether risk identification and assessment have been carried out and relevant forms have been formed 检查是否开展风险辨识和评估，并形成相关表格 | 变更工作已按要求完成
|  | 5.2.5 The risk assessment team members should have certain risk assessment ability and work experience, including but not limited to safety, process, equipment, operation, electrical equipment, design and other personnel to participate, to ensure that the change risk is fully identified and effective risk control measures are developed. 进行风险评估的团队成员应具备一定风险评估能力和工作经验，包括但不限于安全、工艺、设备、操作、电仪、设计等人员参加，确保充分识别变更风险，制定有效风险控制措施。 | Check if team members is made up of the right person to attend 检查团队成员是否由合适的人员组成 | 人员符合
| 5.3 Alteration process 变更审批 | 5.3.3 After the change risk assessment is approved, it shall be countersigned by the centralized management department and other departments involved. 变更风险评估审批通过后，由归口管理部门及其他所涉及的部门进行会签。 5.3.4 General changes are reviewed by relevant functional departments and approved by company leaders. 一般变更由相关职能部门进行审核，公司领导进行批准。 5.3.5 The SafetyCase shall be updated according to the requirements of the government, and shall be implemented after examination and approval by the competent government department. 重大变更按政府要求，更新 SafetyCase，并经政府主管部门审核批准后实施。 | Check if risk assessment approval process includes countersigning by relevant departments, and if change level follows the relevant requirement 检查风险评估审批流程是否包括相关部门的会签，变更级别是否符合相关要求 | 符合
| 5.4 Alteration implementation 变更实施 | 5.4.4 In the process of change implementation, if there may be a large security risk, emergency plans should be prepared in advance, and the preparation of various emergency measures should be implemented. 变更实施过程中，如可能产生较大的安全风险，应提前编制应急预案，并在实施中落实各项应急措施的准备情况。 | Check if emergency plans are prepared for high-risk changes. 检查是否针对高风险变化准备好了应急预案。 | 已有配套预案
| 5.6 Acceptance of changes 变更的验收 | 5.6.1 After the implementation of the change, the centralized management department shall organize relevant departments to carry out the acceptance of the change. Acceptance includes an assessment of the conformity of the change with the intended effect. The acceptance work shall not exceed 90 days after the change is put into use. After acceptance,fill in the Change Acceptance Form. 变更实施结束后，由归口管理部门组织相关部门对变更进行验收工作。 验收包括对变更与预期 效果符合性的评估。验收工作不应超过变更投用后 90 天。 验收后填写《变更验收表》。 | Check if post-implementation acceptance is completed within 90 days and documented. 检查实施后验收是否在90天内完成并记录。 | 符合要求
| 5.7 The application of the change 变更的投用 | 5.7.1 The change department shall conduct beneficiary training and inform the personnel who may be affected by the change, including the purpose, function, content and operation methods of the change, possible risks and impacts in the change, risk control measures, and similar accident cases. 变更部门应对变更可能受影响的人员进行受益人培训和告知，培训内容包括变更目的、作用、变更内容及操作方法、变更中可能的风险和影响、风险的管控措施、同类事故案例等。 | Check if training is conducted for affected personnel on changes, risks, and controls. 检查是否对受影响的人员进行了有关变化、风险和控制的培训。 | 培训记录建全
环境班XXXX离职后，XXXX转副班长岗位，未提供转岗培训记录。 抽查XXX员工培训档案，2024年再培训时长不符合公司制度要求
| 5.8 Acceptance and closure 变更关闭 | 5.8.1 After the implementation of the change, the change department shall timely update the PID drawings, operating procedures, risk assessment, interlocking logic diagrams and other documents involved in the change, and archive the records involved in the change process. 变更实施后，变更部门应及时更新变更涉及的 PID 图纸、操作规程、 风险评价、 联锁逻辑图等文件资料，并将变更过程涉及的记录资料归档。 归口管理部门建立本专业管理台帐。 | Check if P&ID drawings, procedures, risk assessments, and interlocking logic diagrams are up to date, and if it is shared to operators 检查P&ID图纸、程序、风险评估和联锁逻辑图是否是最新的，以及是否与下发给班组 | 已及时更新
|  | 5.8.2 Change management files shall at least include change application approval form, risk assessment record, change acceptance record, change closure confirmation record and other documents related to change. 变更管理档案至少应包括变更申请审批表、风险评估记录、变更验收记录，变更关闭确认记录和与变更相关的其他文件资料等。 | Check if all required documents related to change management are proper documented 检查与变更管理相关的所有必需文件是否已正确保存、归档 | 已保存归档
| 5.10 Emergency change 紧急变更 | 5.10.3 The emergency change shall be implemented after the on-site person in charge confirms the implementation of risk control measures. Relevant records shall be made during the implementation period, and the change procedures shall be completed within 48h after the implementation according to the change procedure. 紧急变更经现场负责人确认落实风险管控措施后实施，实施期间应做好相关记录，在实施后48h内按变更流程补办变更手续。 | Confirm that emergency changes are properly documented and procedures completed within 48 hours. 确认紧急变更已正确记录并且程序已在48小时内完成。 | 已按要求执行
Occupational Health Management 职业卫生 | Identification and assessment of occupational hazard factors 职业病危害因素识别与评估 | 5.2.2 The department’s evaluation team members must reviewed the task activity list, discuss each task activity and work step in detail to conduct an Health Risk Assessment. The identification results shall be recorded in the “HYBN-T7-08-4006-2024-1 Health Risk Assessment (HRA) Record Form”. 各部门评价小组成员按照作业活动清单，对每项作业活动和作业步骤逐项讨论，进行职业病危害风险评估，辨识结果列入《HYBN-T7-08-4006-2024-1职业健康危害因素评估分析 （HRA）记录表》。 | Operational Activities and Steps: Ensure all operational activities and steps are identified and discussed item by item with the evaluation team members according to the checklist. 作业活动及步骤: 确保所有作业活动和作业步骤均被识别，并按清单逐项与评价小组成员讨论 | 符合要求
|  |  | Identification of Occupational Disease Hazard Factors: 1. Identify potential occupational disease hazards, including chemical, physical, biological, ergonomic, and psychological factors. 2. Assess the likelihood of hazards based on workplace environment, operational methods, and exposure duration. 职业病危害因素辨识： 1.识别可能存在的化学、物理、生物、人体工学及心理因素等职业病危害。 2.结合作业环境、操作方式、接触时间等因素，确认危害的可能性。 | 符合要求
|  |  | Risk Assessment: 1. Evaluate the risk level of occupational disease hazards using risk assessment methods (e.g., severity of hazard, exposure frequency, and duration). 2. Record the current hazard control status for each operational step and analyze whether further improvements are needed. 风险评估 1.依据风险评估方法（如危害严重程度、暴露频率、接触时间等），评估职业病危害风险等级。 2.记录各作业步骤的危害控制现状，并分析是否需进一步改进。 | 符合要求
|  |  | Inspection of Control Measures: 1.Determine the effectiveness of existing protective measures (engineering, administrative, and personal protective equipment). 2.Verify compliance with occupational health management systems and emergency response plans. 控制措施检查 1.现有防护措施（工程、行政、个体防护）是否有效。 2.是否有合规的职业健康管理制度和应急预案。 | 符合要求
|  |  | Records and Documentation: 1. Ensure that hazard identification results and assessment data are fully recorded in the “HYBN-T7-08-4006-2024-1 Occupational Health Hazard Assessment (HRA) Record Form.” 2. Ensure the record form is properly filled out with accurate data for future review and improvement. 记录与归档 1.确保辨识结果和评估数据完整记录在《HYBN-T7-08-4006-2024-1 职业健康危害因素评估分析（HRA）记录表》。 2.确保记录表填写规范，数据准确，以便后续审查和改进。 | 符合要求
| Management of occupational hazards 职业病危害因素管理 | 5.3.1 Quality Analysis Department is responsible for monitoring occupational disease hazards and inputting the data into LIMS system. 质量检验部负责职业病危害因素监测，检测、评价结果录入LIMS系统。 | Confirm whether monitoring is conducted according to the 2025 Occupational Health Monitoring Points and whether the evaluation results are entered into the LIMS system on time. 是否按照2025年职业健康监测点进行监测并按时把评价结果录入LIMS系统。 | 已按要求执行
|  | 5.3.4.2 Each execution department shall notify employees the monitoring results of occupational disease hazards of the work they are engaging in by using monitoring bulletin boards. 各执行部门HSE专业以监测告示牌的方式向员工告知本岗位职业病危害因素监测结果。 | Check if occupational hazard monitoring results are publicly posted at the workplace. 检查现场是否有公告职业危害因素监测结果 | 外操室外墙上已张挂
|  | 5.3.4.3 Monitoring results of occupational hazard results (i.e. Quality Inspection Report) shall be published in the Occupational Health notice board and updated within 5 working days. 职业病危害因素监测结果（质检报告单）应在职业健康公告栏展示并在5个工作日内完成更新 | Ask the employees if they know where to check the occupational hazard monitoring results. Do they know when the results will be available? If the data exceeds the limit, will it be communicated during the pre-shift meeting, and will employees be reminded to take protective measures? 询问员工是否知道哪里查职业危害因素监测结果？是否知道什么时候结果出来？数据超标是否班前会进行宣贯并提醒员工做好防护措施？ | 抽查提问4人基本了解
|  | 5.3.7.1 Warning signboards with Chinese and English warning instructions must be place where there may be serious occupational disease hazards. 在可能产生严重职业病危害作业岗位的醒目位置,设置警示标识和中、英文警示说明。 | Ensure warning signs are in place for areas with potential over-limit exposure. 现场有可能超标的地点是否有相关的警示标识 | 现场标识张挂齐全
|  | 5.3.7.4 When signing labor contracts with employees, the HR Dept. shall truthfully inform employees of the occupational hazards that may arise in the work position process and its consequences, occupational disease prevention measures, etc., and state clearly in the labor contracts. 人力资源部在与员工签订劳动合同时，应当将工作岗位过程中可能产生的职业病危害及其后果、职业病防护措施等如实告知员工，并在劳动合同中写明 | Confirm that the department has proper record-keeping procedures. 部门是否做好归档？ | 部门不涉及
|  | 5.6.3.1 Operation protection 作业防护 （4）Operators must check the condition of the gas mask filters before using and department safety engineer must regularly check on the validity of the gas mask filters. 员工必须在使用滤毒盒前检查滤毒盒的状况，部门安全工程师必须定期检查过滤器的有效性 | Are employees aware of when to replace gas filter cartridges and how to conduct a face seal check on masks? Are managers conducting regular inspections of gas filter cartridge validity in gas cabinet? 员工是否知道什么时候更换滤毒盒，是否知道怎么对口罩进行气密性检查？管理人员是定期检查气防柜的滤毒盒的有效期？ Check expiry of gas filters, gas mask in emergency cabinet 检查紧急柜中的气体滤毒盒和防毒面具的有效期 | 滤毒盒没过期，员工知晓如何检查
|  | 5.6.4 Dust protection 粉尘防护 5.6.5 High temperature protection 高温防护 5.6.6 Acid and alkali protection 酸碱防护 | Are employees aware of which PPE is required for different toxic and hazardous work environments? Do employees understand the potential health effects of these toxic and hazardous gases? 对各种有毒有害工作环境，是否知道是用什么劳动防护用品进行防护？ 询问员工是否知道这些有毒有害气体对人员会造成什么伤害？ | 提问员工知晓
|  | 5.6.7.2 All personnel engaged in radiation-related work are required to wear a personal radiation dosimeter (RPL) as specified. The RPL must be measured monthly to ensure that the annual radiation dose does not exceed 20 mSv. 凡从事辐射相关工作人员，按要求佩戴个人辐射剂量计（简称RPL） 每月对RPL进行计量检测，确保年辐射剂量不超过20mSv。 | Ensure radiation-exposed personnel wear RPL (Radiation Personal Dosimeter) when working in radiation environments. 检查辐射人员接触辐射工作环境时是否佩戴RPL | 本月无射线作业
|  | 5.6.7.3 Departments involved in radiation-related work should equip radiation protective suits and related materials in the gas cabinet. 凡设计从事辐射相关工作的部门应在气防柜内配置辐射防护服相关物资。 | Verify whether the relevant departments are properly equipped with radiation safety measures. 相关部门是否配备？ | 无配备
| Occupational Health Archive 职业健康档案 | Departments shall establish OH Archives, and fill in the requisition and issuance in the accounts; 部门应建立本部门员工个人职业健康档案 | Whether department establish OH archive for employees and update annually 是否建立员工职业健康体检档案并一年一更新 | 已建立并及时更新
|  | 5.3.4.4 Monitoring results of occupational hazard results shall be recorded in the Occupational Health archives and updated once every year. 职业病危害因素监测结果应存档入职业健康档案并每年更新一次。 | Has an occupational health examination file been established for employees? Are health records updated regularly? Are health records established for new employees? Are on-the-job medical examination results updated in the records? Radiation personnel medical records updated yearly in OH archive? 是否建立员工职业健康体检档案 是否档案有滚动更新 检查新人是否建立健康档案 在岗体检结果是否更新在档案里 辐射岗位人员体检结果是否有更新到档案里？ | 档案已建立
|  | Departments must regularly update employee's medical check-up information into the OH archives 部门应定期更新职业健康体检信息 | Whether department update OH medical information regularly 是否定期更新员工职业健康体检信息 | 已按人员回国情况做好体检更新
| Work Injury Management 工伤管理 | Recognition of Work Injuries工伤认定 （1）In the event of a work-related injury or an occupational disease, the company representative shall complete the “Work Injury Identification Application Form” and submit it within 30 days. 员工发生工伤或罹患职业病，公司代理人填写《工伤认定申请表》在30天内提出申报; | Is the “Work Injury Identification Application Form” completed by the company representative after an employee sustains a work injury or is diagnosed with an occupational disease? Is the application submitted within the required 30-day period? Are the relevant records and submission documents complete, properly formatted, and archived for future reference? 是否在员工发生工伤或确诊职业病后，由公司代理人填写《工伤认定申请表》？申请是否在规定的30天内提交？相关记录和申报材料是否完整、规范，并存档备查？ | 未发生工伤
| Management on atmospheric pollution 大气污染管理 | 5.4.2.1 (1) Develop waste gas control and emission indicators and relevant operation specifications. 制定废气控制排放指标与相关操作规程。 | Whether to formulate the department's exhaust gas management system (operating procedures for abnormal working conditions) 是否制定本部门废气管理制度（异常工况操作规程） | 部门不存在废气排放
|  | 5.4.2.1(2) Optimize the production process and operation management to ensure the up-to-standard discharge of all types of waste gas. 优化生产工艺与操作管理，确保各类废气达标排放标准。 | 1. Check the LIMS waste gas emission monitoring data to see if the atmospheric pollutant emission data meets the standards. 2. If the waste gas emission exceeds the standard, analyze the reasons for exceeding the standard and optimize and improve the production process and operation management. 1.查LIMS废气排放监测数据，大气污染物排放数据是否达标。 2.废气排放超标是否分析超标原因，是否对生产工艺与操作管理进行优化和技改。 | 部门不存在废气排放
|  | 5.4.2.2 (3) The purging of the device during startup and shutdown shall be airtight purging, and the waste gas from the purging shall be discharged into the flare system and recovered by the gas cabinet as possible. 装置开工、停工中吹扫采用密闭吹扫，吹扫废气应排往火炬系统，尽量由气柜回收。 | 1. Check the HSE control plan for start-up and shutdown to see whether the plan has formulated requirements for closed purge work. 2. Check the site to see whether the closed purge management requirements for start-up and shutdown plans are strictly implemented. 1.查开停工HSE管控方案，方案是否制定密闭吹扫工作要求。 2.查现场，是否严格落实开、停工方案密闭吹扫管理要求。 | 已按要求执行
|  | 5.4.2.1(7) In case of any failure of the waste gas treatment facilities and monitoring facilities, the de-partment in charge of which shall timely repair them and put into use according to the proce-dures and report to the HSE Dept. 废气处理设施、监测设施出现故障，所在部门应按程序及时修复投用，并报告HSE管理部。 | 1. Check the report to see if any failure of the exhaust gas treatment facilities and monitoring facilities has been reported to the HSE Management Department. 2. Check the maintenance plan and maintenance records to see if the maintenance plan has been submitted in a timely manner. 1.查报告，废气处理设施、监测设施出现故障是否报告HSE管理部。 2.查维修计划和维修记录，是否及时提报维修计划。 | 部门不存在废气排放
|  | 5.4.2.2 (1) Environmental protection plans shall be formulated for startup and shutdown. Predictions on atmospheric pollutants that may be emitted shall be carried out. Scheme measures to con-trol and reduce atmospheric pollutants shall be taken. And the scheme for startup and shut-down must be reviewed and approved by the relevant departments and leaders. 开停工应制定环保方案，对可能排放的大气污染物进行预测，应有控制与减少大气污染物的方案措施，开、停工方案须经相关部门与领导审批。 | Check the environmental protection plan for the shutdown 1. Whether the plan contains air pollutant control measures. 2. Whether the plan has been approved by relevant departments. 查开停工环保方案 1.方案内容是否制定大气污染物控制措施。 2.方案是否经相关部门审批。 | 已制定
| Noise management 噪声管理 | 5.6.4 The amount of steam purging shall be controlled for shutdown purging of the produc-tion equipment to reduce the noise of steam emptying to pollute the surrounding environment. 生产装置停工吹扫要控制蒸汽吹扫量，减少蒸汽放空的噪声污染周边环境。 | 1. Check the HSE control plan for the shutdown of the device, and whether a purge plan has been formulated for the steam purge and venting of the device, and whether it has been approved by the HSE Management Department. 2. Check the site and monitor whether the noise at the factory boundary exceeds the standard. 1.查装置停工HSE管控方案，装置停工蒸气吹扫放空是否制定吹扫方案，并经HSE管理部审批。 2.查现场，监测厂界噪声是否超标。 | 已制定
|  | 5.6.6 The environmental monitoring station of the Quality Analysis Dept. shall monitor the noise at boundary in accordance with the analysis plan. 质量检验部环境监测站应对厂界噪声按照分析计划进行监测。 | Check LIMS to see whether the Quality Inspection Department has completed the factory boundary noise monitoring according to the annual environmental monitoring plan. 查LIMS，质检部是否按年度环境监测计划完成厂界噪声监测。 | 噪声已按要求检测
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (11) Equipment and pipelines must be equipped with silencing facilities on the purging vent nozzle to prevent the noise from exceeding standard to cause disturbances to residents. 设备、管线吹扫放空口必须加消音设施，杜绝噪声超标扰民事件发生。 | Check the site to see whether the equipment and pipeline purge vents have been equipped with silencer facilities as required. 查现场，设备、管线吹扫放空口是否按要求增加消音设施。 | 消音设施齐全
| Management on environmental protection facilities 环保设施管理 | 5.8.1.2 Environmental protection facilities must be ensured to operate normally. No one may shut down, idle, or dismantle them without authorization. 环境保护设施必须确保正常运转，任何人员不得擅自停运、闲置、拆除。 | Check the site to see whether the environmental protection facilities are operating normally and whether they have been shut down, idled or demolished without permission. 查现场，环保设施是否正常运转，未经许可是否存在停运、闲置和拆除。 | 正常运转
|  | 5.8.1.3 Environmental protection facilities shall be incorporated into the Company’s equip-ment and facilities management. 环保设施纳入公司设备设施管理。 | Check the equipment management ledger and maintenance records to see whether environmental protection facilities are included in the equipment and facility management, and are regularly inspected and maintained. 查设备管理台账和维护记录，是否将环保设施纳入设备设施管理，并定期检查、维护。 | 清污分流正常运转无污染
|  | 5.8.2.1 The environmental protection facilities and on-line automatic monitoring instruments shall operate in strict accordance with the operation specifications, and the operating parame-ters shall meet the design requirements. 环境保护设施、在线自动监控仪表运行严格按照操作规程执行，操作参数符合设计要求。 | 1. Check the operating procedures, whether the environmental protection facilities and online automatic monitoring instruments have formulated operating procedures, and whether the management requirements of "start first and stop later" are implemented. 2. Check the operating parameters and whether the parameter settings are in accordance with the design. 1.查操作规程，环保设施和在线自动监控仪表是否制定操作规程，是否落实先开后停管理要求。 2.查操作参数，参数设置是否符合设计。 | 部门不涉及
|  | 5.8.2.2 The operators of environmental protection facilities and on-line automatic monitoring instruments must be qualified after the job-specific training and obtain the work license be-fore operating. 环境保护设施、在线自动监控仪表运行的操作人员必须经过岗位培训合格，取得上岗证后方可操作。 | Check the operator's job certificate and whether the operators of environmental protection facilities and online automatic monitoring instruments have received job training and obtained certificates before taking up their posts. 查操作人员上岗证书，环境保护设施、在线自动监控仪表运行的操作人员是否经过岗位培训并取证上岗。 | 部门不涉及
|  | 5.8.2.3 In case of any abnormal operation of environmental protection facilities and on-line automatic monitoring instruments, the production and operation department must promptly find out the causes of abnormalities and make adjustment to ensure a qualified pollutant dis-charge, and shall inform the Scheduling & Dispatch Dept. and the HSE Dept. of the causes of abnormalities by mail. 环境保护设施、在线自动监控仪表运行异常，生产运行部门要及时查清异常原因并调整，确保污染物排放合格，对异常原因以邮件形式告知计划调度部、HSE管理部。 | If there are any abnormalities in the operation of environmental protection facilities or online automatic monitoring instruments, please notify the Planning and Coordination Department and the HSE Management Department via email. 环境保护设施、在线自动监控仪表运行异常，是否邮件通知计调部和HSE管理部。 | 部门不涉及
|  | 5.8.2.5 In case of any fault, damage or defect found in the environmental protection facilities and on-line automatic monitoring instruments, the production and operation department shall promptly deal with them. If they cannot be solved, it shall report in time to the HSE Dept. and the Equipment Management Dept. to jointly solve the problem. 生产运行部门发现环境保护设施、在线自动监控仪表存在故障、损坏、缺陷时，及时处理，如无法解决应及时汇报HSE管理部和机械动力部共同解决。 | 1. Whether environmental protection facilities and online automatic monitoring instruments are handled in a timely manner when they are faulty, damaged or defective. 2. Whether environmental protection facilities and online automatic monitoring instruments are reported to the HSE Management Department when they are faulty, damaged or defective. 3. Whether environmental protection facilities and online automatic monitoring instruments are recorded in the environmental protection facility operation management ledger when they are faulty, damaged or defective. 1.环保设施、在线自动监控仪表存在故障、损坏、缺陷时，是否及时处理。 2.环保设施、在线自动监控仪表存在故障、损坏、缺陷时，是否汇报HSE管理部。 3.环保设施、在线自动监控仪表存在故障、损坏、缺陷时，是否在环保设施运行管理台账中记录。 | 清污分流正常运转无污染
|  | 5.8.2.6 In the event that the environmental protection facilities and on-line automatic monitor-ing instruments are scheduled to be shut down for overhaul or comparison monitoring, the shutdown report form shall be submitted to the Scheduling & Dispatch Dept. and the HSE Dept. for review and approval at least 24 hours in advance; unplanned shutdown for overhaul due to sudden events shall be promptly reported to the Scheduling & Dispatch Dept. and the HSE Dept. by telephone. See appendix for the shutdown report form. 环境保护设施、在线自动监测仪表计划停运检修或比对监测，至少提前24h将停运报告表报告计划调度部、HSE管理部审批；因突发性事件停车的非计划停运检修，应及时电话报告计划调度部、HSE管理部。 | 1. Check the comparison report to see whether the online automatic monitoring instrument is compared and monitored according to the annual environmental monitoring plan frequency requirements. 2. During the comparison monitoring period, whether the process is adjusted to be stable and the external emission index monitoring is qualified. 3. Whether the environmental protection facilities are shut down for maintenance and whether they are reported to the HSE Management Department for approval in advance. 1.查比对报告，是否按年度环境监测计划频次要求对在线自动监测仪表进行比对监测。 2.比对监测期间，是否调整工艺至稳定，且满足外排指标监测合格。 3.环保设施停运检修，是否提前报告HSE管理部审批。 4.因突发性事件导致的环保设施非计划停运检修，是否及时电话报告HSE管理部。 | 部门不涉及
|  | 5.8.2.7 The production and operation department shall establish and perfect the manage-ment ledgers of environmental protection facilities and on-line automatic monitoring instru-ments, set obvious name and description marks on the site, and shall not practice falsification on the operating conditions and monitoring data. 生产运行部门应当建立健全环境保护设施、在线自动监控仪表的管理台账，现场要有明显的名称、说明标识，不得对运行工况和监测数据弄虚作假。 | 1. Check the environmental protection facility records to see whether a management record of environmental protection facilities (including online automatic monitoring instruments) has been established. 2. Check the environmental monitoring data to see if there is any data fraud. 1.查环保设施台账，是否建立环保设施（包括在线自动监控仪表）管理台账。 2.查环境监测数据，是否存在数据弄虚作假。 | 含油污水送水有记录
|  | 5.8.2.8 The production and operation department shall set routing inspection sites to regular-ly conduct routing inspection on environmental protection facilities and on-line automatic mon-itoring instruments, and make routing inspection records. 生产运行部门应当设定巡检站点，定时巡检环境保护设施、在线自动监控仪表，并做好巡检记录。 | 1. Check the site to see if there are inspection points for environmental protection facilities. 2. Check the inspection records to see if environmental protection facilities are inspected on time. 1.查现场，环保设施是否设置巡检点。 2.查巡检记录，环保设施是否按时巡检。 | 含油污水井及水沟在巡检路线内
|  | 5.8.2.9 The production and operation department shall check the data upload of the on-line automatic monitoring instruments once at least every 2 hours per shift. In case of any abnor-mal data transmission, the causes shall be found out and reported to the HSE Dept. by the shift on duty. 生产运行部门每班至少2小时检查一次在线自动监控仪表数据上传情况，数据传输异常时，应查清原因，当班报告HSE管理部。 | 1. Check the system or management requirements to see if the data upload of online automatic monitoring instruments is checked every 2 hours. 2. Set alarms to remind employees when data transmission is abnormal. 3. When data transmission is abnormal, find out the cause and report it to the HSE management department. 1.查制度或管理要求，是否落实每2小时检查一次在线自动监控仪表数据上传情况。 2.数据传输异常是否设置报警提醒员工。 3.数据传输异常时，原因是否查明并报告HSE管理部。 | 部门不涉及
|  | 5.8.2.10 The production and operation department shall organize the self-inspection on envi-ronmental protection facilities and on-line automatic monitoring instruments at least once a month, and send the self-inspection report to the HSE Dept., the contents of which shall in-clude the operation status of the facilities, the discharge of pollutants, the sampling and moni-toring status and the continuous operation records. 生产运行部门每月至少组织一次对环境保护设施、在线自动监控仪表的自查，并将自查报告发给HSE管理部。内容包括：设施的运行状况、污染物排放情况、取样和监测情况、连续运行记录等。 | 1. Check the self-inspection report to see whether self-inspection of environmental protection facilities and online automatic monitoring instruments is organized every month and a self-inspection report is formed. 2. Whether the content of the self-inspection report meets the system requirements. 3. Whether the self-inspection report is sent to the HSE Management Department. 1.查自查报告，是否每月组织对环保设施、在线自动监控仪表开展自查，并形成自查报告。 2.自查报告内容是否满足制度要求。 3.自查报告是否发给HSE管理部。 | 部门不涉及
|  | 5.8.2.12 Be responsible for the management and operation of on-line automatic monitoring instruments, and submit the self-inspection, checking and mandatory verification reports to the HSE Dept. on time. 质量检验部、仪表控制部负责在线自动监控仪表管理和运行，应按时向HSE管理部提交自查、校核、强检报告。 | Check the self-inspection, calibration and compulsory inspection reports of online automatic monitoring instruments, and whether the quality inspection department and instrument control department submit relevant reports on time. 查在线自动监控仪表自查、校核、强检报告，质量检验部、仪表控制部是否按时提交相关报告。 | 部门不涉及
|  | 5.8.2.13 The HSE Dept. and relevant departments have the right to supervise the operation of the environmental protection facilities, and the production and operation department shall faithfully reflect the operation conditions. HSE管理部及相关部门有权监督环境保护设施运行情况，生产运行部门应如实反映运行情况。 | Check the environmental protection facility operation and management records to see whether they truthfully reflect the operation status of the environmental protection facilities. 查环保设施运行管理台账，是否如实反映环保设施运行情况。 | 是
部门废弃物管理台账中未见空油桶/化学品桶的转移处置记录。
部门未建立烟气（烟尘）监测数据统计台帐。
| Management on environmental protections in startup and shutdown as well as maintenance and repair 开停工及检维修环保管理 | 5.9.1.2 Detailed environmental protection management measures shall be given in the schemes of device startup and shutdown as well as maintenance and repair. 装置开、停工、检维修方案中应有详细的环保管理措施。 | Check whether measures are taken to prevent materials in the plan 检查开停工方案，检查相关环境保护措施 | 符合要求
|  | 5.9.1.3 The environmental protection devices shall be started up first and shut down later to ensure the effective disposal of pollutants. 环保装置应做到先开后停，确保污染物得到有效地处置。 | Check the site to see whether the environmental protection devices follow the principle of start-first-stop. 查现场，环保装置是否遵循先开后停原则。 | 遵循
|  | 5.9.1.5 During the period of startup and shutdown as well as maintenance and repair, all ab-normal discharge of pollutants shall be conducted in an orderly manner by applying for ap-proval. 在开停工及检维修期间，所有异常排污进行排污申请，有序排放。 | During start-up, shutdown, inspection and maintenance, abnormal pollution discharge is carried out in accordance with the approval requirements, and discharged in an orderly manner according to the prescribed emission volume during the prescribed time period. 在开停工及检维修期间，异常排污是否按照审批要求执行，在规定时段按规定排放量，有序排放。 | 已按要求执行
|  | 5.9.2.4 Equipment that may cause pollution to clean effluent systems shall be provided with a special cleaning field for diverting wastewater from clean water during the maintenance and repair work. 有可能造成清净下水系统污染的设备应设立专门的清洗场，保证检维修期间的清污分流。 | Whether the flushing equipment is in the proper position to prevent the flushing material from entering the rainwater system 冲洗设备是否在合适的位置，防止冲洗物进入雨水系统 | 位置合适
|  | 5.9.2.5 The stacking sites shall be set up for solid wastes which shall be well-marked by classification to properly keep the solid wastes to prevent pollution. 设立固体废物堆放场所，分类做好标识，妥善保管固体废物，防止发生污染。 | The maintenance work is completed, whether the site is completed and the materials are cleaned up, and whether the waste generated is disposed of in compliance with regulations 检修作业完工，现场是否工完料尽场地清，产生的废弃物是否合规处置 | 符合
|  | 5.9.3.4 It is strictly prohibited to discharge sump oil, various residual liquid, etc. into sewage pipelines, open trenches or rainwater drainage systems. 严禁将污油、各类残液等排入污水管线、明沟或雨排系统。 | Check the scene to see if there is any dirty oil or various residual liquids entering the sewage pipes, open ditches or storm drains. 查现场，是否存在污油、各类残液进入污水管线、明沟或雨排。 | 不存在
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (1) The desulfurization device and the sulfur-containing sewage system as well as equipment like the towers and containers that are in contact with the sulfur-containing and ammonia-containing media in the shutdown device shall be deodorized by the use of effective additives before the purging. 对停工装置中的脱硫装置和含硫污水系统及接触含硫、氨介质的塔、容器等设备在吹扫前使用有效助剂进行脱臭处理。 | Check the HSE control plan to see whether the desulfurization device, sulfur-containing wastewater system, and towers, containers and other equipment that come into contact with sulfur-containing and ammonia media are deodorized with effective additives before purging. 查HSE管控方案，脱硫装置和含硫污水系统及接触含硫、氨介质的塔、容器等设备在吹扫前是否使用有效助剂进行脱臭处理。 | 已按要求落实
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (2) The device shall be purged in an airtight manner. 装置吹扫应采取密闭方式。 | Check the purge plan to see if a closed purge plan has been formulated for the device purge. Check the site to see if there is any odor when the device is purged on site. 查吹扫方案，装置吹扫是否制定密闭吹扫方案。 查现场，装置改现场吹扫是否会有异味。 | 无异味
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (4) The flare shall be timely adjusted to eliminate smoke and steam in the shutdown process, so as to ensure safe emission of burnt waste gas to avoid generation of black smoke. 停车过程中，及时调整火炬消烟蒸汽，安全排放燃烧废气，避免冒黑烟。 | Check the scene to see if there is any black smoke coming out of the torch. 查现场，火炬是否存在冒黑烟情况。 | 没有
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到： (5) When the device undergoes purging of the sour gas system, it is first blown to the flare for burning. After the H2S content of the system is less than 10mg/m3 by sampling analysis, and confirmed on the site by the environmental protection management personnel of the HSE Dept., the device can be emptied on the spot. 装置吹扫酸性气系统时，先吹往火炬燃烧，经采样分析系统H2S含量小于10mg/m3，并经HSE管理部环保管理人员现场确认后，装置才可就地放空。 | 1. Check LIMS to see if the H2S sampling analysis is less than 10mg/m3 before the acid gas purge is vented. 2. Check the site to see if there is any odor when the acid gas purge is vented. 1.查LIMS，酸性气吹扫现场放空前H2S采样分析是否小于10mg/m3。 2.查现场，酸性气吹扫现场放空是否有异味。 | 符合要求
|  | 5.9.3.5 In purging and discharge into flare, the following points shall be achieved: 吹扫、放火炬时应做到 (6) Prior to steam purging of towers, tanks and other containers containing benzenes and hydrocarbons, the system must undergo nitrogen displacement and water flushing. After the total hydrocarbon content of the system is less than 0.5％ by sampling analysis, and con-firmed on the site by the environmental protection personnel of the HSE Dept., the system can be emptied on the spot. 含有苯类、烃类的塔、罐及其他容器蒸汽吹扫前，系统必须进行氮气置换和水冲洗，并经采样分析，系统总烃<0.5％，经HSE管理部环保人员现场确认后，方可就地放空。 | 1. Check LIMS to see if the total hydrocarbon sampling analysis of the system is less than 0.5% before the steam purge of towers, tanks and other containers containing benzene and hydrocarbons is vented on site. 2. Check the site to see if there is any odor when the steam purge of towers, tanks and other containers containing benzene and hydrocarbons is vented on site. 1.查LIMS，含有苯类、烃类的塔、罐及其他容器蒸气吹扫现场放空前系统总烃采样分析是否小于0.5％。 2.查现场，含有苯类、烃类的塔、罐及其他容器蒸气吹扫现场放空是否有异味。 | 符合
|  | 5.9.3.6 Steam purging & cleaning, the following points shall be achieved: 蒸煮、清洗时应做到： (4) Equipment cleaning water is prohibited from discharging into the rainwater drainage sys-tems. 设备清洗水禁止排入雨排系统。 | Check on site to see whether the equipment cleaning water enters the rainwater drain. 查现场，设备清洗水是否进入雨排。 | 没进入
|  | 5.9.3.10 During the period of shutdown, synchronous monitoring shall be carried out on the sewage outlets, waste gas emissions and the ambient atmosphere. 停工期间应对污水排放口情况、废气排放情况和环境大气进行同步监测。 | Check LIMS to see whether the Quality Inspection Department conducts simultaneous monitoring of sewage outlet conditions, waste gas emissions and ambient atmosphere as required. 查LIMS，质检部是否按要求对对污水排放口情况、废气排放情况和环境大气进行同步监测。 | 是
|  | 5.9.4 Maintenance and repair stage 检维修阶段 5.9.4.1 Effective measures shall be taken to prevent the residual materials in the dismantling process of the equipment from falling to the ground. 应采取有效措施，防止设备拆解过程的残余物料落地。 | 1. Check the maintenance plan to see whether the maintenance plan effectively identifies the risk of residual materials during the equipment disassembly process and whether corresponding control measures are formulated. 2. Check the site to see whether there are residual materials on the ground during the equipment disassembly. 1.查检维修方案，检维修方案制定是否有效识别出设备拆解过程存在残余物料的风险，是否制定相应控制措施。 2.查现场，设备拆解是否存在残余物料落地。 | 已制定方案
|  | 5.9.4 Maintenance and repair stage 检维修阶段 5.9.4.2 The equipment that may cause pollution to the clean effluent system shall be sent to the designated place for cleaning to prevent pollution to the rainwater drainage system. 应将有可能造成清净下水系统污染的设备送到指定地点清洗，防止污染雨排系统。 | 1. Check the maintenance plan to see whether the maintenance plan identifies that sewage will pollute the rainwater drainage system during equipment cleaning, and whether the equipment is considered to be sent to a designated location for cleaning. 2. Check the site to see whether effective measures are taken during the cleaning process to prevent pollution of the rainwater drainage system if the equipment cannot be sent to a designated location for cleaning. 1.查检维修方案，检维修方案制定是否辨识设备清洗过程中污水会污染雨排系统，是否考虑将设备送到指定地点清洗。 2.查现场，设备如果无法送到指定地点清洗，清洗过程是否采取有效措施防止污染雨排。 | 移送至指定地点
|  | 5.9.4 Maintenance and repair stage 检维修阶段 5.9.4.3 During maintenance and repair of the device, the rainwater drainage system, wastewater pool and sewage discharge pipe network of the device shall be maintained and repaired simultaneously. 装置检维修时，应同时对装置的雨排系统、废水池和排污管网进行检维修。 | Check the maintenance plan to see whether the drainage system, wastewater tank and sewage pipe network of the device have been inspected and maintained. 查检修计划，是否对对装置的雨排系统、废水池和排污管网进行检维修。 | 已排计划
|  | 5.9.4.4 The process medium wastes (such as polymer, sludge, bottom mud , waste catalysts, etc.) cleaned out of the equipment and pipelines shall be transported to the designated place in time. 设备及管线清理出的工业固体废物（如聚合物、油泥、底泥、废催化剂等）要及时运至指定场所， | 1. Check the HSE control plan to see if the storage location and management requirements of industrial solid waste are clearly stated in the plan. 2. Check the site to see if the industrial solid waste cleared from the equipment and pipelines is transported to the designated location as required. 1.查HSE管控方案，方案中是否明确工业固废的存放地点和管理要求。 2.查现场，设备及管线清理出的的工业固废是否按要求运至指定场所。 | 已移至指定地点
|  | 5.9.4.5 Waste classification management shall be strictly implemented, where hazardous wastes and general wastes shall be collected separately, valuable materials and valueless ma-terials collected separately. 严格执行垃圾分类管理，危险废物与一般废物分开收集，有价物料与无价物料分开收集。 | Check the site to see whether hazardous waste and general industrial solid waste are collected separately. Check whether valuable materials and non-valuable materials are collected separately. 查现场，危险废物、一般工业固废是否分开收集。有价值物料与无价值物料是否分开收集。 | 已做好垃圾分类
|  | 5.9.4.6 The pool cleaning and tanks cleaning shall be carried out under schemes. The envi-ronmental protection measures shall have undergone the environmental protection review, and measures of sludge “reduction” shall be taken. The generated sludge with higher oil con-tent shall be sent to the Power Dept. for treatment, and those with lower oil content and with liquidity shall be sent to the sewage farm of Utilities Dept. 清池、清罐有方案，环保措施经过环保审查，采取油泥“减量化”措施。产生的油泥含油率较高的送往热电部处理，含油率较低且有流动性的送往公用工程部污水处理场。 | 1. Whether an environmental protection plan has been formulated for pool and tank cleaning and has been reviewed by the environmental protection department of the HSE department. 2. Whether an application has been submitted for sludge disposal and whether it has been disposed of in accordance with the approval requirements. 1.清池、清罐是否制定环保方案，并经HSE部环保专业审查。 2.油泥处置是否提交申请，并按审批要求处置。 | 已按要求落实
|  | 5.9.4.7 During the period of shutdown for maintenance, the vegetation shall not be damaged or polluted, nor the soil or surface water shall be polluted. 停工检修期间不得损坏和污染植被，不污染土壤与地表水。 | Check the site to see whether the vegetation has been damaged or contaminated during the maintenance process, and whether the soil and surface water have been polluted. 查现场，检修过程是否存在损坏、污染植被，是否存在污染土壤和地表水的情况。 | 不存在污染
|  | 5.9.4.8 All departments shall be responsible for the environmental protection management of the external construction teams and the maintenance and operation assurance teams within the scope of their own departments. 各部门负责本部门范围内的外来施工队伍、维护保运队伍的环保管理。 | 1. Conduct on-site inspections to check whether the environmental protection management of external construction teams and maintenance and transportation teams is in place. 1.现场检查，外来施工队伍、维护保运队伍的环保管理是否执行到位。 | 已按要求执行
| Management on environmental protection statistics 环保统计管理 | 5.12.2.2 All departments shall undertake the responsibility for the accuracy of the statistical data of their own departments, and report the environmental protection statistics of the pre-ceding month to the HSE Dept. each month. 各部门对本部门统计数据准确性负责，每月上报上月环保统计给HSE管理部。 | Check the environmental statistics ledger to see whether the statistical data is accurate, whether it has been reviewed by the department, and whether it has been submitted to the HSE Management Department on time. 查环保统计台账，统计数据是否准确，是否经本部门审核，并按时提交HSE管理部。 | 已按要求执行
|  | 5.12.3 Management on environmental protection signs 环保标识管理 Refer to the provisions of HSE Signs in Section 5.11 of the HSE Comprehensive Manage-ment System. 参照《HSE综合管理制度》中第5.11部分HSE标识的规定。 5.11.3.2 It is not allowed to remove or damage HSE signs without permission and it shall replace missed or damaged ones in a timely manner. Personnel who cause intentional damage shall be punished in accordance with the Company’s related assessment regulations. HSE标识不得擅自拆动或损坏，若发现缺损，应按要求及时更换，故意损害者，按照公司考核相关规定进行处罚。 | Check the on-site environmental protection signs to see if any are missing or damaged. 查现场环保标识，是否存在缺失、损坏。 | 无缺失，损坏
| Environmental accident and incident management 环保事故、事件管理 | Refer to the provisions of Accident and incident management in Section 5.17 of the HSE Comprehensive Management System. 参照《HSE综合管理制度》中第5.17部分事故、事件管理的规定。 5.17.5.1 incident and accident management requirements事故、事件报告要求 After an operation department accident or incident occurs, the occurrence department shall immediately report to the dispatch room, the person in charge of the department and the HSE Management Department, and submit a Preliminary Report Form of Accident (Incident) to the HSE Department via email within 24 hours. 发生事件、运行部级事故后，发生部门应立即报告调度室、本部门负责人和HSE管理部，24小时内通过邮箱向HSE管理部提报《事故（事件）初步报告表》。 | Check the "Preliminary Report Form for Accident (Incident)" to see whether the report is submitted within the time limit. 查《事故（事件）初步报告表》，是否按时限要求报告。 | 已按要求落实
|  | 5.17.6.1 Incident investigation 事件调查 Where the incident submitted to the "Accident (incident) Preliminary Report Form", the occurrence department shall organize the incident investigation within one week after the occurrence of the incident, prepare the incident investigation record form, and the department shall file the record. 凡提报《事故（事件）初步报告表》的事件，发生部门应在事件发生后一周内组织事件调查，编写《事故（事件）报告表》，报HSE管理部。 | Check the "Accident (Event) Report Form" to see whether an investigation into the environmental incident has been organized and the "Accident (Event) Report Form" has been submitted within the time limit. 查《事故（事件）报告表》，是否按时限要求对环保事件组织调查并提交《事故（事件）报告表》。 | 已按要求执行
|  | 5.17.6.2 Accident investigation 事故调查 （1）In the event of an departmental level accident, each operation department shall organize its own investigation, and the competent department of the company may participate in the investigation. After the investigation is completed, the accident department shall fill in the Accident (Incident) Report Form and submit it to the HSE Department. If the accident involves several departments, the competent department shall organize the investigation, and the competent department shall designate relevant departments to fill in the Accident (Incident) Report Form and submit it to the HSE Department. 发生运行部级事故，由各运行部自行组织调查，公司主管部门可参与调查。调查完成后，事故发生部门填写《事故（事件）报告表》，并提报HSE管理部；事故涉及到几个部门的，由主管部门组织调查，并由主管部门指定相关部门填写《事故（事件）报告表》，并提报HSE管理部。 | Check the "Accident (Incident) Report Form" to see whether an investigation into the environmental accident has been organized and the "Accident (Incident) Report Form" has been submitted within the time limit. 查《事故（事件）报告表》，是否按时限要求对环保事故组织调查并提交《事故（事件）报告表》。 | 已按要求执行
|  | 5.17.6.3 In the course of accident liability investigation, it shall make a thorough investigation of direct cause, indirect cause, primary cause and minor cause of the accident, and define personnel directly responsible for the accident and those mainly responsible for the accident. 在调查事故责任时，要查清事故的直接原因、间接原因，分清事故的直接责任者、主要责任者。 | Check the "Accident (Incident) Report Form" to find out the direct and indirect causes, and distinguish the direct and main responsible persons for the accident. 查《事故（事件）报告表》，是否查清直接原因、间接原因，分清事故的直接责任者、主要责任者。 | 已按要求执行
|  | 5.17.7.2 After the handling of accidents and events, the department shall fill in the Registration Form of Accident (Event) Four and Accident Management Statistics Account, and other relevant departments shall fill in the Implementation Form of Accident Prevention Measures of Relevant Departments according to the requirements of the HSE Management Department, and report to the HSE Management Department for record. 事故、事件处理结束后，部门填写《事故（事件）四不放过登记表》、《事故管理统计台帐》，其他相关部门按HSE管理部的要求填写《相关部门事故防范措施落实表》，并上报HSE管理部备案。 | 1. Check the "Four No-Let-Go Registration Form for Accidents (Events)" and "Accident Management Statistical Ledger". 2. Check the "Accident Prevention Measures Implementation Form of Relevant Departments". 1.查《事故（事件）四不放过登记表》、《事故管理统计台帐》。 2. 查《相关部门事故防范措施落实表》。 | 已按要求执行
|  | 5.17.7.3 In case of cover-up, false reporting and deliberate delay in reporting of an accident, intentional destruction of accident site, concealing of accident truth, objection to receive investigation or provide any information and data without justified reasons, punishment shall be aggregated. 事故发生后隐瞒不报、谎报、故意拖延不报、故意破坏事故现场、隐瞒事故真相，或者无正当理由，拒绝接受调查以及拒绝提供有关情况和资料的，加重处理。 | 1. Ask on-site employees whether there are any environmental accidents (incidents) that are concealed, falsely reported, or deliberately delayed. 2. Check the accident site to see if the accident site has been deliberately damaged. 3. Investigate and collect evidence and interview personnel about environmental accidents (incidents) to see if there are any who refuse to accept the investigation and refuse to provide relevant information and materials. 1.询问现场员工，是否存在环保事故（事件）隐瞒不报、谎报、故意拖延不报。 2.查事故现场，是否存在事故现场被故意破坏情况。 3.环保事故（事件）调查取证及人员访谈，是否存在拒绝接受调查以及拒绝提供有关情况和资料的。 | 无瞒报
| Environmental protection training 环保培训 | Refer to the provisions of HSE education, training and competency building in Section 5.10 of the HSE Comprehensive Management System. 参照《HSE综合管理制度》中第5.10部分HSE教育、培训和能力建设的规定。 5.10.3.1 New employees in operation positions shall receive 3 level HSE training, the time is 72 academic hours, and the annual refresher training time is not less than 20 academic hours, and they can only take the post after passing the examination. 生产操作岗位新员工应接受三级HSE培训，时间为72学时，每年再培训时间不少于20学时，并经考试合格后方可上岗。 | Check whether the HSE training materials and annual retraining contents of the operation department and team level cover environmental protection content. 查运行部、班组级HSE培训材料和年度再培训内容，是否涵盖环保内容。 | 涵盖环保内容
|  | 5.10.4 Special HSE training HSE专项培训 HSE special training shall be implemented temporarily according to the training plan formulated by the HSE Management Department and the Operation Department or according to the current safety situation according to the needs of employees and the different characteristics of each position, including but not limited to safety, environmental protection, occupational health, fire protection, accident cases, emergency plans, laws and regulations, HSE operating procedures, etc. HSE专项培训应根据员工需求和各岗位不同特点按照HSE管理部及运行部制定的培训计划或根据当前安全形势临时实施，包括但不限于安全、环保、职业健康、消防、事故案例、应急预案、法律法规、HSE操作规程等。 | Check the department's annual HSE training plan and records to see whether an environmental protection training plan has been developed and completed. 查部门年度HSE培训计划和记录，是否制定并完成环保培训计划。 | 已制定
|  | 5.10.6.1 Before contractor personnel enter the factory, the HSE Management Department will conduct Level I HSE training. Before entering the operation area of each unit, the Operation Department will conduct Level II HSE training. After the training, the contractors must pass the examination and conduct safety briefings before operation. Each operating department should keep training records. 承包商人员入厂前由HSE管理部实施一级HSE培训，进入各装置区域作业前由运行部实施二级HSE培训，培训结束经考试合格，作业前进行安全交底后方可作业。各运行部门应做好培训记录。 | Check the contractor's Level 2 HSE training materials to see if they include environmental protection content and requirements. 查承包商人员二级HSE培训材料，是否包含环保内容和要求。 | 已包含
| Assessment on environmental protection 环保考核 | Refer to the provisions of HSE Assessment in Section 5.15 of the HSE Comprehensive Man-agement System. 参照《HSE综合管理制度》中第5.15部分HSE考核的规定。 5.15.2 Each department shall refer to the Company's "Performance Appraisal Measures" or refine the performance appraisal system of its own department to assess, reward and punish the HSE work of its own department, and establish the HSE assessment reward and punishment ledger. 各部门引用公司《绩效考核办法》或细化为本部门绩效考核制度，对本部门的HSE工作情况进行考核奖惩，并建立HSE考核奖惩台帐。 | Check the HSE assessment reward and punishment ledger to see whether the content of the ledger involves environmental protection professional rewards and punishments. 查HSE考核奖惩台帐，台账内容是否涉及环保专业奖惩。 | 涉及
| Environmental protection management during operation 作业过程环境保护管理 | 5.18.2 After the work is completed, each construction unit must ensure that the site is "clean", that is: there is no relics, no oil pollution, and no damage on the construction site; the site is cleared after the work is completed and the local department inspects it. 作业结束后，各施工作业单位必须做到现场“三无一清”，即：施工现场无遗物、无油污、无损害；工完料尽场地清，由属地部门监督落实。 | Check the implementation of “three no’s and one clear” at the work site. 查作业现场“三无一清”执行情况。 | 现场按规定落实
|  |  | 芳烃装置D550A装卸剂作业HSE管控方案未对粉尘开展环境因素识别并制定措施。同类问题在岐化反应器换剂HSE管控方案中也存在。 | 本月未涉及
|  | 5.18.3 Each unit should formulate an emergency operation plan for the installation operation process, and take emergency preventive measures to reduce the impact and impact on pollu-tion control facilities and sewage treatment systems, ensure treatment effects, and prevent the occurrence of environmental pollution accidents and incidents. 各单位在制定HSE管控方案时，应识别环境风险，制定环境保护措施，预防环境污染事故、事件的发生。 | 1. Check the HSE control plan for the operation to see whether environmental risks are identified and environmental protection measures are formulated. 2. Check the operation site to see whether the environmental protection requirements in the HSE control plan are effectively implemented. 1.查作业HSE管控方案，是否识别环境风险并制定环保措施。 2.查作业现场，HSE管控方案中的环保要求是否得到有效落实。 | 涉及
| 5.1 Management principles and content 管理原则和内容 | 5.1.1 The principle of "whoever is in charge is responsible" for gas control and safety work shall be adhered to, and a responsibility system for gas control and safety shall be implemented. Every employee has the obligation to maintain fire prevention safety, protect fire prevention facilities, prevent fires, report fire alarms, provide fire protection and participate in emergency rescue. 消气防安全工作坚持“谁主管、谁负责”的原则，实行消气防安全责任制。每位员工都有维护消气防安全、保护消气防设施、预防火灾、报告火警、气防救护和参加应急救援的义务。 | Whether the fire safety responsibility system has been implemented and the responsible persons for fire protection at the post have been clearly identified; 是否落实防火安全责任制，并明确岗位消防责任人； | 防火台账已记录
|  |  | 1、Whether fire safety knowledge training is organized for each post so that personnel can master firefighting skills; 是否组织各岗位学习进行消防安全知识培训，使人员掌握消防技能； 2、Whether the department leaders participated and whether the relevant records were signed by the leaders 部门领导是否参与，相关记录有无领导签名 | 近期正在进行消防竞赛人员选拔，今日马斯鲁知识竞赛成绩70.5分
| 5.3.11 Purchase requisition of fire-fighting equipment, facilities and appliances 消气防设备 设施器材申购 | 5.3.11.5 Each professional department shall regularly purchase fire fighting equipment, facilities and spare components in advance according to the need of the site conditions and to meet the need of the situation. The purchase requisition of fire fighting equipment, facilities and appliances shall be performed as per the company’s relevant regulations. 各专业管理部门根据现场需要，定期提前提报消防设备、器材以及备品备件，以满足现场的需要，消防设备设施器材的申购工作按公司有关规定执行。 | According to the needs of the site, whether fire-fighting equipment, instruments and spare parts are purchased regularly in advance to meet the needs of the site; 根据现场需要，是否定期提前采购消防设备、器材以及备品备件，以满足现场的需要； | 已报采购计划
| 5.3.16 Management of the use and suspension of fire-fighting water 消防水使用、停用管理 | 5.3.11.2 When the production equipment is stopped for maintenance, the fire-fighting water system shall not be stopped. If the system needs to be stopped, it shall be restored before the equipment is stopped for maintenance. If it’s really necessary to stop the use of fire water when the equipment id stopped for maintenance, it shall be approved by the leader in charge of the company. 生产装置停产检修时，消防水系统不得停用；若需停用，应在装置停产检修前予以恢复；装置停产检修期间，确需停用消防水，应由公司主管领导批准。 | When the production equipment is shut down for maintenance, is the fire water system shut down? 生产装置停产检修时，消防水系统是否停用； | 不停用
| 5.4 Fire-fighting publicity and training 消防宣传和培训 | 5.4.2 Fire-fighting training for personnel, such as new recruits, transferees and re-appointed staff, shall be performed during the three-level safety education activity by the responsible person of three-level safety education. 新员工、转岗、复岗等人员的消防内容培训，由三级安全教育负责人在进行三级安全教育时予以落实。 | Whether the fire protection content training for new employees, transfer personnel, returning personnel, etc. is implemented during the third-level safety education, and whether records are kept and archived; 新员工、转岗、复岗等人员的消防内容培训，是否在进行三级安全教育时予以落实，并留有记录，存档管理； | 已按要求记录并存档
| 5.4 Fire-fighting publicity and training 消防宣传和培训 | 5.4.3 Each department shall perform fire safety education at least once per quarter. The content shall mainly include: fire-fighting laws and regulations, fire safety institutions and operation rules, fire hazardousness and fire safety measures of the department, operation of fire fighting facilities, knowledge and skills concerning fire alarm, warning, separation, fire extinguishment and rescue, self-rescue and self-escape. 各部门每季度不少于1次消防安全教育；培训内容主要包括：消防法律法规；消防安全制度和操作规程；本部门的火灾危险性和防火措施；消防设施使用和操作；报警、警戒、隔离、灭火以及救人、自救与逃生的知识和技能。 | Whether fire safety education is implemented as required, whether the training content is sound, and whether records are kept and archived; 消防安全教育是否按要求落实，培训内容是否健全，并留有记录，存档管理； | 本月消防技能选拔成绩已记录存档
| 5.4 Fire-fighting publicity and training 消防宣传和培训 | 5.4.4 Operators of fire fighting facilities and appliances shall receive special training in operation skills, learn and master corresponding operation skills, and may take the post after passing the examination. 消防设备设施操作人员应经过专门的操作技能培训，学习掌握相应的操作技能，经考试合格后上岗。 | Whether firefighting skills training is carried out to learn and master the corresponding operating skills, and whether they can take up their posts after passing the examination, and whether records are kept and archived; 是否开展消防技能培训，学习掌握相应的操作技能，经考试合格后上岗，并留有记录，存档管理； | 本月已完成消防演练并记录
| 5.5 Fire prevention inspections and hidden danger management 消气防监督检查和隐患治 理 | 5.5.1.1 Fire inspections shall be divided into the company-level and the department-level inspections. At company level, there are monthly fire inspections, special inspections and professional inspections, while at department level, fire inspections are daily inspections. 防火检查分为公司级和部门级；公司级防火检查分为每月防火检查、专项检查和专业检查；部门级防火检查为日检。 5.5.1.2 Contents of fire inspections shall include situations of key fire-control places, integrity of fire fighting equipment, facilities, systems and appliances, shift taking of fire control room, escape routes, safety exits, fire lanes and other unimpeded conditions, integrity of archives and accounts, ratification of fire hazard. 防火检查的内容包括消防重点部位情况；消防设备设施系统及器材的完好性；消防控制室值班情况；疏散通道、安全出口、消防车通道等畅通情况；档案和台账完整情况；火灾隐患整改情况等。 | Whether department-level fire prevention inspections are strictly implemented, and records are kept and archived; 是否严格落实部门级防火检查，并留有记录，存档管理； | 防火检查记录表已按要求记录
| 5.6 Fire-fighting drills, fire-fighting and rescue 消气防演练与灭火救灾 | 5.6.1.1 Each operation department shall formulate special emergency plans and on-site response scheme according to specific situations, and organize regular drills as per the company’s relevant regulations. 各运行部应根据具体情况制定专项应急预案和现场处置方案；各运行部按照公司相关规定定期组织演练。 | Whether on-site emergency drills are conducted regularly; 是否定期开展现场应急演练； | 按年度演练计划每月一次
| 5.6 Fire-fighting drills, fire-fighting and rescue 消气防演练与灭火救灾 | 5.6.1.2 Schemes shall be made before the drills. The scheme shall include scene of the drill, emergency response, gas protection and first aid, evacuation and processing. Fire brigades, gas protection departments and security departments shall also be invited to cooperate in the drill to make it more practical. 演练前，应编制演练方案，方案包括演练情景、应急响应、火灾扑救、气防急救、人员疏散、工艺处理等内容，也可邀请消防、气防、安保配合演练，以使演练更加贴合实际。 | Whether a drill plan has been prepared; whether the content of the plan is complete; 是否编制演练方案；方案内容是否齐全； | 年度演练方案齐全
| 5.6 Fire-fighting drills, fire-fighting and rescue 消气防演练与灭火救灾 | 5.6.1.3 After the drill, it shall be summarized and the emergency response plan of the accident shall be revised according to the drills. 演练结束后应进行总结，根据演练情况对事故应急方案进行修订。 | Whether a summary is conducted after the drill and a summary report is kept; 演练结束后是否进行总结，并留有总结报告； | 本月演练总结已收集
| 5.7 Construction of emergency rescue teams 应急救援队伍建设 | 5.7.2.2 Number of the volunteer fire brigade shall not be less than 60% of the total personnel of the department, and external operators shall be the member of it. In case of personnel changes, each department shall report the change to the HSE Dept. within 30 days. 志愿消防队的人数不少于本部门职工总数的60%，外操人员应为志愿消防队员；若有人员变动，各部门应在30天内将变动情况上报HSE管理部。 | Whether a volunteer fire brigade has been established and whether the number of volunteer fire brigades meets the requirements; 是否建立志愿消防队,志愿消防队的人数是否满足要求； Whether changes in department personnel have been reported to the HSE Management Department within 30 days;" 部门人员发生变动后是否在30天内将变动情况上报HSE管理部； | 上岗员工基本全部为支援消防人员
| 5.8 Fire-fighting records and archives 消防记录和档案 | 5.8.1 Each department shall be responsible for establishing a department-level fire-fighting archive and submit it to the HSE Dept. which shall establish a company-level fire-fighting archive. 各部门负责建立本部门消防档案，并上报HSE管理部，HSE管理部建立公司消防档案。 | Whether departmental fire protection files are established; 是否建立部门消防档案； | 已建立档案
炼油三部演练记录未及时增添到消防档案中，炼油四部火灾情况和演练记录未及时增添到消防档案中，档案管理需要进一步完善
| 5.8 Fire-fighting records and archives 消防记录和档案 | 5.8.2 Content of fire fighting archives shall include basic information on fire safety , fire safety management and other documentations. 消防档案内容包括消防安全基本情况、消防安全管理情况等文件材料。 | Whether the contents of the fire protection files are complete; 消防档案内容是否完备； | 内容建全